## SCG
Church Gate
|  | Units | Quantity | Price | Total Price
5 | INDOOR LIGHTING
The Lighting System specified herein, must conform to Specifications, in addtion to the description given in respective items of BOQ, whether explicitly specified or not. In case of contradiction between specifications and description in BOQ, the most stringent of the condition will prevail.
5.1 | Supply, Installation, Testing and Commissioning of the following Luminaires including all accessories and all fixing accessories shall be as per Specification.
All wiring within the luminarries must be with Fire Resistant LSZH Wires, as per requirements of Specifications.
A | General purpose, basic batten luminaries (Similar to Philips catalogue No. TMS 122, 2x28 T5 OR equivalent) for 'TL'D fluorescent lamp with - Surface mounting arrangement on wall or ceiling - Single piece channel construction made of powder coated CRCA white sheet steel - Lamp holder brackets and HF electronics ballast. The luminaries should be suitable for 2 x 28W Tubular Flourescent Lamp and supplied with 2 Nos 28W Tubular Flourescent lamps. | NO | 60
B | General purpose, basic batten luminaries (Similar to Philips catalogue.No. TMC 122, 1x28 OR equivalent) for 'TL'D fluorescent lamp with - Surface mounting arrangement on wall or ceiling - Single piece channel construction made of powder coated CRCA white sheet steel - Lamp holder brackets and HF electronics ballast. The luminaries should be suitable for 1x28W Tubular Flourescent Lamp and supplied with 1 No. 28W Tubular Flourescent lamps. | NO | 30
C | General purpose basic batten luminaries (Similar to Philips catalogue.No. TMS 122, 2x28W OR equivalent with vitreous enamelled reflector) for 'TL'D fluorescent lamp with - Surface mounting arrangement on wall or ceiling - Single piece channel construction made of powder coated CRCA white sheet steel - Vitreous Enamelled Reflector of white colour - Lamp holder brackets and HF electronics ballast. The luminaries should be suitable for 2x28W Tubular Flourescent lamp and supplied with 2 Nos 28W Tubular Flourescent lamps. | NO | 480
D | Mirror Optic Recess mounted luminaries (Similar to Bajaj catalogue.No BTMRA 4x14 OR Philips OR equivalent subject to approval by ER | NO | 50
E | Efficient, low glare, surface mounted luminaries (Similar to Philips Catalogue No. MPF 922 / 1 X 70W) with integral gear, electrochemically brightened and anodized high purity aluminium reflector of symmetrical type. The luminaries must be non corrosive pressure die cast aluminium housing and white powder coated finish and must be suitable for ceiling mounting. It should have cover made of heat resistant toughened glass and the must be conforming to Ingress Protection Classification of IP 65 (for dust and moisture protection). The luminaries should be suitable for, and supplied with, One No 70W Metal Halide lamp . | NO | 50
F | Mirror Optic Recess mounted luminaries (Similar to Philips catalogue.No TBS 669 / 228 D6 OR equivalent) with housing made of white powder coated CRCA sheet steel, accommodating all electrical accessories pre-wired upto a terminal block. It should have high efficiency mirror optic reflector of high quality aluminium with parabolic side reflector, 3D cross lamallae with fresnell top and concave lower contour. The luminaries should be suitable for 2 x 28W Tubular Flourescent Lamps and supplied with 2 Nos 28W Tubular Flourescent Lamps. | NO | 110
F | Mirror Optic Recess mounted luminaries (Similar to Philips catalogue.No TCS 255 / 2x28 OR Keselec equivalent subject to approval by ER, Catalog no Pharma (Sym/Asym) 2x28 ) with housing made of white powder coated CRCA sheet steel, accommodating all electrical accessories pre-wired upto a terminal block. It should have high efficiency mirror optic anodised aluminium reflector for symmetrical and asymmetrical light distribution and must conform to Ingress Protection Classification of IP 54 (for dust and moisture protection). The luminaries should be suitable for 2 x 28W Tubular Flourescent Lamps and supplied with 2 Nos 28W Tubular Flourescent Lamps. | NO | 280
H | General purpose basic batten luminaries (Similar to Philips catalogue.No. TCW 450, 1x28 OR equivalent) for 'TL'D fluorescent lamp with - Surface mounting arrangement on wall or ceiling - Single piece channel construction made of powder coated CRCA white sheet steel - Lamp holder brackets and HF electronics ballast - Wire Guard to protect the lamp The luminaries should be suitable for 1 x 28W Tubular Flourescent lamp and supplied with 1 Nos 28W Tubular Flourescent lamps. | NO | 160
I | Recessed Circular Down Light luminaries (Similar to Philips catalogue.No FBH 145 / 218 OR equivalent with satin finished, anodised aluminium reflector and clear glass cover. The luminaries should be suitable for 2 x 18 W CFL lamps and supplied with 2 Nos 18W CFL lamps. | NO | 55
J | Mirror Optic, recessed mounted Luminaries (Similar to Philips catalogue.No TBS/TCS 255 / 228 OR equivalent) with housing made of white powder coated CRCA Sheet Steel, accomodating all electrical accessories pre-wired upto a terminal box. It should have high efficiency mirror optic anodised aluminium reflector and must conform to Ingress Protection Classification of IP 54 (for dust and moisture Protection). The Luminaries should be suitable for 2 x 28W Tubular Flourescent lamp and supplied with 2 Nos. 28W Tubular Flourescent Lamp. | NO | 390
K | Supply of Mirror Optic, Surface mounted Luminaries (Similar to Philips catalogue No. TCS 399 / 228 OR equivalent) or equivelent as per approved list, with housing made of powder coated CRCA Sheet Steel, accomodating all electrical accessories . It should have high efficiency mirror optic reflector . The Luminaries should be suitable for 2 x 36W Tubular Flourescent lamp and supplied with 2 Nos. 36W Tubular Flourescent Lamp. | NO | 390
L | Mirror Optic Recess mounted luminaries (Similar to Philips catalogue.No TBS 669 / 128 D6 OR equivalent) with housing made of white powder coated CRCA sheet steel, accommodating all electrical accessories pre-wired upto a terminal block. It should have high efficiency mirror optic reflector of high quality aluminium with parabolic side reflector, 3D cross lamallae with fresnell top and concave lower contour. The luminaries should be suitable for 1 x 28W Tubular Flourescent Lamps and supplied with 1 Nos 28W Tubular Flourescent Lamps. | NO | 10
N | Tunnel luminaire with high impact resistance IK10, IP-65 weather proof type, industrail LED type with housing and fire resistant low smoke halogen free type and non combustible materials (suitable for loop in & loop out with 4x4 sq mm/4x2.5 sq mm cable). similar to Phillips Cat BWP 120 LED 16 CWPC S1 or equivalent as per specifications. | NO | 220
O | Bulk Head luminaries (Similar to Philips Catalogue No FXC 101 OR equivalent) suitable for mounting on wall / ceiling having -Single piece pressure die cast Aluminium housing - Wire Guard made of powder coated MS - Heat resistant Glass cover The luminaries must conform to Ingress Protection Classification of IP 54 (for dust and Moisture Protection ). The luminaries should be suitable for 1 x 9W CFL lamp and supplied with 1 No. 9W CFL lamp and control accessories. | NO | 25
Q | Surface/Suspended type moisture proof diffuser luminiare with housing made of grey, high impact resistant polycarbonate, with Non-ageing gasket consisting of 2-component polyurethane foam. Difuser made of one piece injection moulded high impact resistant polycarbonate also computer optimised internal prismatic structure for precise direction of light and glare reduction, with difuser clips made of stainless steel, roll formed galvanised steel reflector that is enamelled white and can be suspended from either side of the housing. Suitable for 2x28W FTL Lamp prewired upto a terminal box with lamp. Having IP 65 (similar to Philips catalogue No. TCW 450 \ 2 x 28W HF or equivalent) and supplied with 2 Nos 28W Tubular Flourescent Lamps. | NO | 10
FL-1 | Compact, sturdy, general purpose floodlight luminaries (Similar to Philips catalogue. No TEMPO3 SWF 330 SK type OR equivalent) with integral gear, electrochemically brightened and anodized high purity aluminium reflector of symmetrical type. The luminaries must be adjustable with rugged, non corrosive pressure die cast aluminium housing and black powder coated finish and must be suitable for column mounting. It should have cover made of heat resistant toughened glass and the must be conforming to Ingress Protection Classification of IP 65 (for dust and moisture protection). The luminaries should be suitable for, and supplied with, One No 250W Sodium Vapour lamp. | NO | 20
FL-2 | Compact, sturdy, general purpose floodlight luminaries (Similar to Philips catalogue. No TEMPO3 MWF 330\250 AK HPI -T PLUS lamp OR equivalent) with integral gear, electrochemically brightened and anodized high purity aluminium reflector of symmetrical type. The luminaries must be adjustable with rugged, non corrosive pressure die cast aluminium housing and black powder coated finish and must be suitable for column mounting. It should have cover made of heat resistant toughened glass and the must be conforming to Ingress Protection Classification of IP 65 (for dust and moisture protection). The luminaries should be suitable for, and supplied with, One No 250W Metal halide lamp.(For double height area) | NO | 10
5.2 | Supply, Installation,Testing and Commission of Separate set of Nickel Cadmium battery with battery charger compatibles with all types of fixture mentioned above except Metal Halide & Flood Light type of fixtures with back-up as specified in specification. | NO | 443
5.6 | External station Lighting
5.6.1 | Supply,Installation,testing and Commisioning of Hot dip galvanised Octagonal poles similar to -Bajaj Make cat ref. BOP-1040 height 10 mtr ,top dia 100mm,Bottom dia 200mm,plate thickness 4 MM, Base plate 310x310x20 mm foundation PCD 310 mm size 4x25mm dia ,space for cable termination block at the top half of the polewith cover plate | No | 10
5.6.2 | Supply ,Installation,Testing and commisioning of 1x250W HPSV MH-T(Die cast aluminium top ,maintanable street light luminarie with curved toughened glass 7 pot optic reflector with IP 66 Lamp Compartment.Complete.Similar to 338/250W ( similar to Velocity model of Phillips make) | No | 10
a | Supply,Testing and Installation of 250 W HPSV Lamp (Phillips/Osram Make) | No | 5
b | Supply,Testing and Installation of 250 W Metal halide Lamp (Phillips/Osram Make) | No | 5
5.6.3 | Supply of 75mm dia HDPE pipe confirming to PN-4 boring of road channel area by using open trench method and laying of HDPE pipe properly continuously jointed restoring the surface where pitting is done ,to original position. | Mtr | 15
5.6.4 | Supply of 75mm dia HDPE pipe confirming to PN-4 boring of road channel area by using trench less method and laying of HDPE pipe properly continuously jointed restoring the surface where pitting is done ,to original position. | Mtr | 15
5.6.5 | Supply and installation of GI Bracket single arm,painted, 1m over hang. | No | 15
5.6.6 | Supply and installation of GI Bracketdouble arm,painted 1m over hang | No | 5
5.6.7 | Supply and installation of GI Bracket Tripple arm,painted,1m over hang | No | 5
5.6.8 | Supply and laying of 6 SWG wire along with the cable | Mtr | 50
5.6.9 | Providing and fixing thermo plastic poly carbonate pole boxex confirming to IP-65 degree of protection, along with 16A MCB and 5 way connector and 2 No. cable gland suitable for 4x25 sq.mm cable. | each | 15
5.6.10 | Assembly of pre supplied fitting parts such as choke, bulb, igniter etc ready for energisation and installation of the same on single / double/ tripple GI bracket, fixing of nuts and bolts properly with the help of tower wagon ( Tower wagon shall be arranged by the contractor at his own cost.) | each | 25
5.6.11 | wiring for lumanaries in existing poles with following sizes of unarmoured cu cables from ploe box to each fittings.
| 3x2.5 sq mm | Mtr | 50

## SCG revised
Church Gate revised
|  | Units | Quantity | Price | Total Price
5 | INDOOR LIGHTING
The Lighting System specified herein, must confirm to Specifications, in addtion to the description given in respective items of BOQ, whether explicitly specified or not. In case of contradiction between specifications and description in BOQ, the most stringent of the condition will prevail.
All the items / parts mentioned in relevant clauses of the specifications and not specifically mentioned in BOQ shall be deemed to be included in the quoted rates, unless specifically excluded.
5.1 | Supply, Installation, Testing and Commissioning of the following Luminaires including all accessories and all fixing accessories shall be as per Specification.
All wiring within the luminarries must be with Fire Resistant LSZH Wires, as per requirements of Specifications.
A | Supply of LED 2x2 luminaire with CRCA housing suitable with fully diffused diffuser for general lighting in office areas. The luminaire should have a color consistency SDCM < 5, CRI > 80 and CCT of 6500K. The luminaire shall be compliant with IP20 and IK02 classification. Luminaire shall be designed to emit at least 3600 nominal lumens and an outstanding backlit solution efficacy of atleast 115 lumen/watt and maximum system wattage of 31 Watts. The lumanaire should have outstanding backlit solution efficacy.The luminaire shall be designed so as to ensure lumen depreciation of up to 30% over 50k burning hours @ design ambient temp 45 deg C. The electronic driver used shall have a power factor >0.95 and THD <10% and have options for DALI dimmable too. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Similar to RC380B LED36S -6500 G4 L60 W60 PSU OD. (BOH with False Ceiling Area) | NO | 21
B | Supply of Integral LED 4 ft luminaire with CRCA housing and UV shielded PC Glossy cover. The luminaire should have a color consistency SDCM < 5, CRI > 80 and CCT of 6500K. The luminaire shall be compliant with IP20 classification. Luminaire shall be designed to emit at least 4000 nominal lumens with maximum system wattage of 34 watts at a system efficacy of atleast 120 lumen/watt. The luminaire shall be designed so as to ensure lumen depreciation of up to 30% over 50k burning hours @ design ambient temp 45 deg C. Luminaire to be flickerfree with ripple <5%. The electronic driver used shall have a power factor >0.95 and THD <10% and has high low cutoff with auto restart suitable for an operationg voltage range of 140-270V AC with high voltage cut of 325V. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters.Similar to BN308C LED40S-6500 L120 PSU WH. (BOH without False Ceiling Area) | NO | 455
| Supply of Integral LED 4 ft luminaire with CRCA housing and UV shielded PC Glossy cover. The luminaire should have a color consistency SDCM < 5, CRI > 80 and CCT of 6500K. The luminaire shall be compliant with IP20 classification. Luminaire shall be designed to emit at least 2000 nominal lumens with maximum system wattage of 16 watts at a system efficacy of atleast 120 lumen/watt. The luminaire shall be designed so as to ensure lumen depreciation of up to 30% over 50k burning hours @ design ambient temp 45 deg C. Luminaire to be flickerfree with ripple <5%. The electronic driver used shall have a power factor >0.95 and THD <10% and has high low cutoff with auto restart suitable for an operationg voltage range of 140-270V AC with high voltage cut off at 325V. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters.Similar to BN308C LED20S-6500 L120 PSU WH. |  | 55
C | Supply of LED recessed downlighter with pressure die cast alumium housing . The luminaire should have a color consistency SDCM < 5, CRI > 80 and CCT of 6500K. The luminaire shall be compliant with IP20 and IK02 classification. Luminaire shall be designed to emit at least 1500 system lumens with maximum system wattage of 13.5 Watts. The lumanaire should have outstanding backlit solution efficacy.The luminaire shall be designed so as to ensure lumen depreciation of up to 30% over 50k burning hours @ design ambient temp 45 deg C. The electronic driver used shall have a power factor >0.95 and THD <10% and have operating voltage range from 130-320V. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Similar to DN296B LED15S-6500 PSU WH (Toilets) | NO | 43
D | Supply, installation, testing and commissioning of LED Linear 1x4 recessed fixture - 42 Watt, with a system lumen output of 3000 lumens at an efficacy of >65 lm/W (Similar to Philips Catalogue no. RC869 B W30 L120 LED or equivalent). The luminaire shall have powder coated CRCA housing and light output is by means of Semi High Gloss optics with 3D Lamellae and High Purity Anodized Aluminium mirrors. (Concourse & Platform Public Area) | NO | 698
E | Supply, installation, testing and commissioning of LED trunking system - 40 Watt , with a system lumen output of 4000 lumens and a minimum system efficacy of 100 lumen/watt (Similar to Philips Catalogue no. LL199X 1XDLED40-6500 PSE OD WH or equivalent). The luminaire shall have a extrusion housing and light emitted shall have a CRI>80 with rated system lifetime of 50,000 hours at L70. The extrusion housing shall be available in 4', 8' and 12' sections. (Platform Public Area) | NO | 100
F | Supply, installation, testing and commissioning of surface mounted LED Batten - 38 Watt (Similar to Philips Catalogue no. BN 108C LED 40S PSU CDL WH 919515810658 or equivalent), with a system lumen output of 4000 lumens and a minimum system efficacy of 100 lumen/watt. The luminaire shall have a CRI of greater than 80 with rated system lifetime of 50,000 hours at L70. The luminaire is made of CRCA housing and shall have diffused optics. (BOH without False Ceiling Area) | NO
F | Mirror Optic Recess mounted luminaries (Similar to Philips catalogue.No TCS 255 / 2x28 OR Keselec equivalent subject to approval by ER, Catalog no Pharma (Sym/Asym) 2x28 ) with housing made of white powder coated CRCA sheet steel, accommodating all electrical accessories pre-wired upto a terminal block. It should have high efficiency mirror optic anodised aluminium reflector for symmetrical and asymmetrical light distribution and must conform to Ingress Protection Classification of IP 54 (for dust and moisture protection). The luminaries should be suitable for 2 x 28W Tubular Flourescent Lamps and supplied with 2 Nos 28W Tubular Flourescent Lamps. | NO
H | Supply of Integral LED 4 ftwaterproof luminaire with UV Shielded polycarbonate housing and openable end caps. The luminaire should have a color consistency SDCM < 5, CRI > 80 and CCT of 6500K. The luminaire shall be compliant with IP65 and IK08 classification. Luminaire shall be designed to emit at least 4400 nominal lumens with maximum system wattage of 20 watts at a system efficacy of atleast 120 lumen/watt. The luminaire shall be designed so as to ensure lumen depreciation of up to 30% over 50k burning hours @ design ambient temp 45 deg C. Luminaire to be flickerfree with ripple <5%.The electronic driver used shall have a power factor >0.95 and THD <10% and suitable for an operationg voltage range of 140-270V ACThe electronic driver used shall have a power factor >0.95 and THD <10% and has high low cutoff with auto restart suitable for an operationg voltage range of 140-270V AC with high voltage cut off at 325. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters.Similar to WT201C LED44S-6500 PSU L120 S2(UNDERCROFT AREA) | NO | 156
I | Supply of LED Bulkhead with pressure die cast aluminium housing and PC diffuser. The fixture should have CRI > 80 and CCT of both 6500K. The luminaire shall be compliant with IP65 and IK08 classification. Luminaire shall be designed to emit at least 700 nominal lumens and maximum system wattage of 6.5 Watts. T.The luminaire shall be designed so as to ensure lumen depreciation of up to 30% over 25k burning hours @ design ambient temp 45 deg C. The electronic driver used shall have a power factor >0.9 and THD <20% . Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Similar to WT140W LED7S CW PSU S1 PC.(Shaft Area) | NO | 22
| Supply of LED based Flood light, housing made up of pressure die cast aluminum Alloy with effective thermal management,sturdiness and embossed brand name/logo name of manufacturer. The fixture should have a minimum system efficacy of 110 lumen/Watt and a minimum system lumen output of 13500 lumens and maximum system wattage of 120 Watts.The fixture shall have a CRI of minimum 70. The fixture shall be designed for a system life of 50,000 hours @70% lumen maintenance. Ingress Protection of IP66 (lamp and gear Compartment) and Mechanical Impact Resistance Rating of IK >=05.The fixture driver should have an operating voltage range of 140-270 V with autocut off at 325V, surge protection of >=3KV, PF >0.9 and THD<20%. The fixture should comply with the parameters as per IS10322. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Similar to Philips CAT No. -BVP122 LED135 CW HE NB FG XTFC | NO | 9
J | Mirror Optic, recessed mounted Luminaries (Similar to Philips catalogue.No TBS/TCS 255 / 228 OR Keselec Catalog no.Pharma 2x28HF) with housing made of white powder coated CRCA Sheet Steel, accomodating all electrical accessories pre-wired upto a terminal box. It should have high efficiency mirror optic anodised aluminium reflector and must conform to Ingress Protection Classification of IP 54 (for dust and moisture Protection). The Luminaries should be suitable for 2 x 28W Tubular Flourescent lamp and supplied with 2 Nos. 28W Tubular Flourescent Lamp. | NO | 445
K | Supply of Mirror Optic, Surface mounted Luminaries (Similar to Philips catalogue No. TCS 399 / 228 OR Keselec Catalog no. Airolux DL 2/28W HF) or equivelent as per approved list, with housing made of powder coated CRCA Sheet Steel, accomodating all electrical accessories . It should have high efficiency mirror optic reflector . The Luminaries should be suitable for 2 x 36W Tubular Flourescent lamp and supplied with 2 Nos. 36W Tubular Flourescent Lamp. | NO | 360
L | Mirror Optic Recess mounted luminaries (Similar to Philips catalogue.No TBS 669 / 128 D6 OR Keselec Catalog no.CT lux DL 1x28HF) with housing made of white powder coated CRCA sheet steel, accommodating all electrical accessories pre-wired upto a terminal block. It should have high efficiency mirror optic reflector of high quality aluminium with parabolic side reflector, 3D cross lamallae with fresnell top and concave lower contour. The luminaries should be suitable for 1 x 28W Tubular Flourescent Lamps and supplied with 1 Nos 28W Tubular Flourescent Lamps. | NO | 10
N | Tunnel luminaire with high impact resistance IK10, IP-65 weather proof type, industrail LED type with housing and fire resistant low smoke halogen free type and non combustible materials (suitable for loop in & loop out with 4x4 sq mm/4x2.5 sq mm cable). similar to Phillips Cat BWP 120 LED 16 CWPC S1, as per specifications. | NO | 180
O | Bulk Head luminaries (Similar to Philips Catalogue No FXC 101 OR Keselec Catalog no. KBH 1x9 W) suitable for mounting on wall / ceiling having -Single piece pressure die cast Aluminium housing - Wire Guard made of powder coated MS - Heat resistant Glass cover The luminaries must conform to Ingress Protection Classification of IP 54 (for dust and Moisture Protection ). The luminaries should be suitable for 1 x 9W CFL lamp and supplied with 1 No. 9W CFL lamp and control accessories. | NO | 25
Q | Surface/Suspended type moisture proof diffuser luminiare with housing made of grey, high impact resistant polycarbonate, with Non-ageing gasket consisting of 2-component polyurethane foam. Difuser made of one piece injection moulded high impact resistant polycarbonate also computer optimised internal prismatic structure for precise direction of light and glare reduction, with difuser clips made of stainless steel, roll formed galvanised steel reflector that is enamelled white and can be suspended from either side of the housing. Suitable for 2x28W FTL Lamp prewired upto a terminal box with lamp. Having IP 65 (similar to Philips catalogue No. TCW 450 \ 2 x 28W HF or Keselec make sub 2x28W HF) and supplied with 2 Nos 28W Tubular Flourescent Lamps. | NO | 10
FL-1 | Compact, sturdy, general purpose floodlight luminaries (Similar to Philips catalogue. No TEMPO3 SWF 330 SK type OR Keselec make KSFL/250W/ SON-T) with integral gear, electrochemically brightened and anodized high purity aluminium reflector of symmetrical type. The luminaries must be adjustable with rugged, non corrosive pressure die cast aluminium housing and black powder coated finish and must be suitable for column mounting. It should have cover made of heat resistant toughened glass and the must be conforming to Ingress Protection Classification of IP 65 (for dust and moisture protection). The luminaries should be suitable for, and supplied with, One No 250W Sodium Vapour lamp. | NO | 20
FL-2 | Compact, sturdy, general purpose floodlight luminaries (Similar to Philips catalogue. No TEMPO3 MWF 330\250 AK HPI -T PLUS lamp OR Keselec make KSFL 250W/ HPI-T Plus) with integral gear, electrochemically brightened and anodized high purity aluminium reflector of symmetrical type. The luminaries must be adjustable with rugged, non corrosive pressure die cast aluminium housing and black powder coated finish and must be suitable for column mounting. It should have cover made of heat resistant toughened glass and the must be conforming to Ingress Protection Classification of IP 65 (for dust and moisture protection). The luminaries should be suitable for, and supplied with, One No 250W Metal halide lamp.(For double height area) | NO | 10
5.2 | Supply, Installation,Testing and Commission of Separate set of Nickel Cadmium battery with battery charger compatibles with all types of fixture mentioned above except Metal Halide & Flood Light type of fixtures with 2 hours back-up. | NO | 445

## SCP
Cuffe Parade Station
|  | Units | Quantity | Price | Total Price
5 | INDOOR LIGHTING
The Lighting System specified herein, must conform to Specifications, in addtion to the description given in respective items of BOQ, whether explicitly specified or not. In case of contradiction between specifications and description in BOQ, the most stringent of the condition will prevail.
All the items / parts mentioned in relevant clauses of the specifications and not specifically mentioned in BOQ shall be deemed to be included in the quoted rates, unless specifically excluded.
5.1 | Supply, Installation, Testing and Commissioning of the following Luminaires including all accessories and all fixing accessories shall be as per Specification.
All wiring within the luminarries must be with Fire Resistant LSZH Wires, as per requirements of Specifications.
A | General purpose, basic batten luminaries (Similar to Philips catalogue No. TMS 122, 2x28 T5 OR Keselec Catalog no.Railux 2x28 HF) for 'TL'D fluorescent lamp with - Surface mounting arrangement on wall or ceiling - Single piece channel construction made of powder coated CRCA white sheet steel - Lamp holder brackets and HF electronics ballast. The luminaries should be suitable for 2 x 28W Tubular Flourescent Lamp and supplied with 2 Nos 28W Tubular Flourescent lamps. | NO | 210
B | General purpose, basic batten luminaries (Similar to Philips catalogue.No. TMC 122, 1x28 OR Keselec Catalog no Railux 1x28HF) for 'TL'D fluorescent lamp with - Surface mounting arrangement on wall or ceiling - Single piece channel construction made of powder coated CRCA white sheet steel - Lamp holder brackets and HF electronics ballast. The luminaries should be suitable for 1x28W Tubular Flourescent Lamp and supplied with 1 No. 28W Tubular Flourescent lamps. | NO | 30
C | General purpose basic batten luminaries (Similar to Philips catalogue.No. TMS 122, 2x28W OR Keselec Catalog no. Indilux V 228 HF with vitreous enamelled reflector) for 'TL'D fluorescent lamp with - Surface mounting arrangement on wall or ceiling - Single piece channel construction made of powder coated CRCA white sheet steel - Vitreous Enamelled Reflector of white colour - Lamp holder brackets and HF electronics ballast. The luminaries should be suitable for 2x28W Tubular Flourescent lamp and supplied with 2 Nos 28W Tubular Flourescent lamps. | NO | 480
D | Mirror Optic Recess mounted luminaries (Similar to Bajaj catalogue.No BTMRA 4x14 OR Philips OR Keselec equivalent subject to approval by ER | NO | 90
E | Efficient, low glare, surface mounted luminaries (Similar to Philips Catalogue No. MPF 922 / 1 X 70W) with integral gear, electrochemically brightened and anodized high purity aluminium reflector of symmetrical type. The luminaries must be non corrosive pressure die cast aluminium housing and white powder coated finish and must be suitable for ceiling mounting. It should have cover made of heat resistant toughened glass and the must be conforming to Ingress Protection Classification of IP 65 (for dust and moisture protection). The luminaries should be suitable for, and supplied with, One No 70W Metal Halide lamp . | NO | 50
F | Mirror Optic Recess mounted luminaries (Similar to Philips catalogue.No TBS 669 / 228 D6 OR Keselec Catalog no.CT lux 2x28HF) with housing made of white powder coated CRCA sheet steel, accommodating all electrical accessories pre-wired upto a terminal block. It should have high efficiency mirror optic reflector of high quality aluminium with parabolic side reflector, 3D cross lamallae with fresnell top and concave lower contour. The luminaries should be suitable for 2 x 28W Tubular Flourescent Lamps and supplied with 2 Nos 28W Tubular Flourescent Lamps. | NO | 130
F | Mirror Optic Recess mounted luminaries (Similar to Philips catalogue.No TCS 255 / 2x28 OR Keselec equivalent subject to approval by ER, Catalog no Pharma (Sym/Asym) 2x28 ) with housing made of white powder coated CRCA sheet steel, accommodating all electrical accessories pre-wired upto a terminal block. It should have high efficiency mirror optic anodised aluminium reflector for symmetrical and asymmetrical light distribution and must conform to Ingress Protection Classification of IP 54 (for dust and moisture protection). The luminaries should be suitable for 2 x 28W Tubular Flourescent Lamps and supplied with 2 Nos 28W Tubular Flourescent Lamps. | NO | 280
H | General purpose basic batten luminaries (Similar to Philips catalogue.No. TCW 450, 1x28 OR Keselec Catalog no.Railux 1x28 HF) for 'TL'D fluorescent lamp with - Surface mounting arrangement on wall or ceiling - Single piece channel construction made of powder coated CRCA white sheet steel - Lamp holder brackets and HF electronics ballast - Wire Guard to protect the lamp The luminaries should be suitable for 1 x 28W Tubular Flourescent lamp and supplied with 1 Nos 28W Tubular Flourescent lamps. | NO | 250
I | Recessed Circular Down Light luminaries (Similar to Philips catalogue.No FBH 145 / 218 OR Keselec Catalog no.Nova 2x18 (G)) with satin finished, anodised aluminium reflector and clear glass cover. The luminaries should be suitable for 2 x 18 W CFL lamps and supplied with 2 Nos 18W CFL lamps. | NO | 55
J | Mirror Optic, recessed mounted Luminaries (Similar to Philips catalogue.No TBS/TCS 255 / 228 OR Keselec Catalog no.Pharma 2x28HF) with housing made of white powder coated CRCA Sheet Steel, accomodating all electrical accessories pre-wired upto a terminal box. It should have high efficiency mirror optic anodised aluminium reflector and must conform to Ingress Protection Classification of IP 54 (for dust and moisture Protection). The Luminaries should be suitable for 2 x 28W Tubular Flourescent lamp and supplied with 2 Nos. 28W Tubular Flourescent Lamp. | NO | 70
K | Supply of Mirror Optic, Surface mounted Luminaries (Similar to Philips catalogue No. TCS 399 / 228 OR Keselec Catalog no. Airolux DL 2/28W HF) or equivelent as per approved list, with housing made of powder coated CRCA Sheet Steel, accomodating all electrical accessories . It should have high efficiency mirror optic reflector . The Luminaries should be suitable for 2 x 36W Tubular Flourescent lamp and supplied with 2 Nos. 36W Tubular Flourescent Lamp. | NO | 550
L | Mirror Optic Recess mounted luminaries (Similar to Philips catalogue.No TBS 669 / 128 D6 OR Keselec Catalog no.CT lux DL 1x28HF) with housing made of white powder coated CRCA sheet steel, accommodating all electrical accessories pre-wired upto a terminal block. It should have high efficiency mirror optic reflector of high quality aluminium with parabolic side reflector, 3D cross lamallae with fresnell top and concave lower contour. The luminaries should be suitable for 1 x 28W Tubular Flourescent Lamps and supplied with 1 Nos 28W Tubular Flourescent Lamps. | NO | 10
N | Tunnel luminaire with high impact resistance IK10, IP-65 weather proof type, industrail LED type with housing and fire resistant low smoke halogen free type and non combustible materials (suitable for loop in & loop out with 4x4 sq mm/4x2.5 sq mm cable). similar to Phillips Cat BWP 120 LED 16 CWPC S1, as per specifications. | NO | 260
O | Bulk Head luminaries (Similar to Philips Catalogue No FXC 101 OR Keselec Catalog no. KBH 1x9 W) suitable for mounting on wall / ceiling having -Single piece pressure die cast Aluminium housing - Wire Guard made of powder coated MS - Heat resistant Glass cover The luminaries must conform to Ingress Protection Classification of IP 54 (for dust and Moisture Protection ). The luminaries should be suitable for 1 x 9W CFL lamp and supplied with 1 No. 9W CFL lamp and control accessories. | NO | 25
Q | Surface/Suspended type moisture proof diffuser luminiare with housing made of grey, high impact resistant polycarbonate, with Non-ageing gasket consisting of 2-component polyurethane foam. Difuser made of one piece injection moulded high impact resistant polycarbonate also computer optimised internal prismatic structure for precise direction of light and glare reduction, with difuser clips made of stainless steel, roll formed galvanised steel reflector that is enamelled white and can be suspended from either side of the housing. Suitable for 2x28W FTL Lamp prewired upto a terminal box with lamp. Having IP 65 (similar to Philips catalogue No. TCW 450 \ 2 x 28W HF or Keselec make sub 2x28W HF) and supplied with 2 Nos 28W Tubular Flourescent Lamps. | NO | 10
FL-1 | Compact, sturdy, general purpose floodlight luminaries (Similar to Philips catalogue. No TEMPO3 SWF 330 SK type OR Keselec make KSFL/250W/ SON-T) with integral gear, electrochemically brightened and anodized high purity aluminium reflector of symmetrical type. The luminaries must be adjustable with rugged, non corrosive pressure die cast aluminium housing and black powder coated finish and must be suitable for column mounting. It should have cover made of heat resistant toughened glass and the must be conforming to Ingress Protection Classification of IP 65 (for dust and moisture protection). The luminaries should be suitable for, and supplied with, One No 250W Sodium Vapour lamp. | NO | 20
FL-2 | Compact, sturdy, general purpose floodlight luminaries (Similar to Philips catalogue. No TEMPO3 MWF 330\250 AK HPI -T PLUS lamp OR Keselec make KSFL 250W/ HPI-T Plus) with integral gear, electrochemically brightened and anodized high purity aluminium reflector of symmetrical type. The luminaries must be adjustable with rugged, non corrosive pressure die cast aluminium housing and black powder coated finish and must be suitable for column mounting. It should have cover made of heat resistant toughened glass and the must be conforming to Ingress Protection Classification of IP 65 (for dust and moisture protection). The luminaries should be suitable for, and supplied with, One No 250W Metal halide lamp.(For double height area) | NO | 10
5.2 | Supply, Installation,Testing and Commission of Separate set of Nickel Cadmium battery with battery charger compatibles with all types of fixture mentioned above except Metal Halide & Flood Light type of fixtures with 2 hours back-up. | NO | 443
5.6 | External station Lighting
5.6.1 | Supply,Installation,testing and Commisioning of Hot dip galvanised Octagonal poles similar to -Bajaj Make cat ref. BOP-1040 height 10 mtr ,top dia 100mm,Bottom dia 200mm,plate thickness 4 MM, Base plate 310x310x20 mm foundation PCD 310 mm size 4x25mm dia ,space for cable termination block at the top half of the polewith cover plate | No | 10
5.6.2 | Supply ,Installation,Testing and commisioning of 1x250W HPSV MH-T(Die cast aluminium top ,maintanable street light luminarie with curved toughened glass 7 pot optic reflector with IP 66 Lamp Compartment.Complete.Similar to 338/250W ( similar to Velocity model of Phillips make) | No | 10
a | Supply,Testing and Installation of 250 W HPSV Lamp (Phillips/Osram Make) | No | 5
b | Supply,Testing and Installation of 250 W Metal halide Lamp (Phillips/Osram Make) | No | 5
5.6.3 | Supply of 75mm dia HDPE pipe confirming to PN-4 boring of road channel area by using open trench method and laying of HDPE pipe properly continuously jointed restoring the surface where pitting is done ,to original position. | Mtr | 15
5.6.4 | Supply of 75mm dia HDPE pipe confirming to PN-4 boring of road channel area by using trench less method and laying of HDPE pipe properly continuously jointed restoring the surface where pitting is done ,to original position. | Mtr | 15
5.6.5 | Supply and installation of GI Bracket single arm,painted, 1m over hang. | No | 15
5.6.6 | Supply and installation of GI Bracketdouble arm,painted 1m over hang | No | 5
5.6.7 | Supply and installation of GI Bracket Tripple arm,painted,1m over hang | No | 5
5.6.8 | Supply and laying of 6 SWG wire along with the cable | Mtr | 50
5.6.9 | Providing and fixing thermo plastic poly carbonate pole boxex confirming to IP-65 degree of protection, along with 16A MCB and 5 way connector and 2 No. cable gland suitable for 4x25 sq.mm cable. | each | 15
5.6.10 | Assembly of pre supplied fitting parts such as choke, bulb, igniter etc ready for energisation and installation of the same on single / double/ tripple GI bracket, fixing of nuts and bolts properly with the help of tower wagon ( Tower wagon shall be arranged by the contractor at his own cost.) | each | 25
5.6.11 | wiring for lumanaries in existing poles with following sizes of unarmoured cu cables from ploe box to each fittings.
| 3x2.5 sq mm | Mtr | 50

## scp revised
Cuffe Parade Station Revised
|  | Units | Quantity | Price | Total Price
5 | INDOOR LIGHTING
The Lighting System specified herein, must confirm to Specifications, in addtion to the description given in respective items of BOQ, whether explicitly specified or not. In case of contradiction between specifications and description in BOQ, the most stringent of the condition will prevail.
All the items / parts mentioned in relevant clauses of the specifications and not specifically mentioned in BOQ shall be deemed to be included in the quoted rates, unless specifically excluded.
5.1 | Supply, Installation, Testing and Commissioning of the following Luminaires including all accessories and all fixing accessories shall be as per Specification.
All wiring within the luminarries must be with Fire Resistant LSZH Wires, as per requirements of Specifications.
A | Supply of LED 2x2 luminaire with CRCA housing suitable with fully diffused diffuser for general lighting in office areas. The luminaire should have a color consistency SDCM < 5, CRI > 80 and CCT of 6500K. The luminaire shall be compliant with IP20 and IK02 classification. Luminaire shall be designed to emit at least 3600 nominal lumens and an outstanding backlit solution efficacy of atleast 115 lumen/watt and maximum system wattage of 31 Watts. The lumanaire should have outstanding backlit solution efficacy.The luminaire shall be designed so as to ensure lumen depreciation of up to 30% over 50k burning hours @ design ambient temp 45 deg C. The electronic driver used shall have a power factor >0.95 and THD <10% and have options for DALI dimmable too. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Similar to RC380B LED36S -6500 G4 L60 W60 PSU OD. (BOH with False Ceiling Area) | NO | 131
B | Supply of Integral LED 4 ft luminaire with CRCA housing and UV shielded PC Glossy cover. The luminaire should have a color consistency SDCM < 5, CRI > 80 and CCT of 6500K. The luminaire shall be compliant with IP20 classification. Luminaire shall be designed to emit at least 4000 nominal lumens with maximum system wattage of 34 watts at a system efficacy of atleast 120 lumen/watt. The luminaire shall be designed so as to ensure lumen depreciation of up to 30% over 50k burning hours @ design ambient temp 45 deg C. Luminaire to be flickerfree with ripple <5%. The electronic driver used shall have a power factor >0.95 and THD <10% and has high low cutoff with auto restart suitable for an operationg voltage range of 140-270V AC with high voltage cut of 325V. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters.Similar to BN308C LED40S-6500 L120 PSU WH. (BOH without False Ceiling Area) | NO | 513
| Supply of Integral LED 4 ft luminaire with CRCA housing and UV shielded PC Glossy cover. The luminaire should have a color consistency SDCM < 5, CRI > 80 and CCT of 6500K. The luminaire shall be compliant with IP20 classification. Luminaire shall be designed to emit at least 2000 nominal lumens with maximum system wattage of 16 watts at a system efficacy of atleast 120 lumen/watt. The luminaire shall be designed so as to ensure lumen depreciation of up to 30% over 50k burning hours @ design ambient temp 45 deg C. Luminaire to be flickerfree with ripple <5%. The electronic driver used shall have a power factor >0.95 and THD <10% and has high low cutoff with auto restart suitable for an operationg voltage range of 140-270V AC with high voltage cut off at 325V. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters.Similar to BN308C LED20S-6500 L120 PSU WH. |  | 116
C | Supply of LED recessed downlighter with pressure die cast alumium housing . The luminaire should have a color consistency SDCM < 5, CRI > 80 and CCT of 6500K. The luminaire shall be compliant with IP20 and IK02 classification. Luminaire shall be designed to emit at least 1500 system lumens with maximum system wattage of 13.5 Watts. The lumanaire should have outstanding backlit solution efficacy.The luminaire shall be designed so as to ensure lumen depreciation of up to 30% over 50k burning hours @ design ambient temp 45 deg C. The electronic driver used shall have a power factor >0.95 and THD <10% and have operating voltage range from 130-320V. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Similar to DN296B LED15S-6500 PSU WH (Toilets) | NO | 36
D | Supply, installation, testing and commissioning of LED Linear 1x4 recessed fixture - 42 Watt, with a system lumen output of 3000 lumens at an efficacy of >65 lm/W (Similar to Philips Catalogue no. RC869 B W30 L120 LED or equivalent). The luminaire shall have powder coated CRCA housing and light output is by means of Semi High Gloss optics with 3D Lamellae and High Purity Anodized Aluminium mirrors. (Concourse & Platform Public Area) | NO | 363
E | Supply, installation, testing and commissioning of LED trunking system - 40 Watt , with a system lumen output of 4000 lumens and a minimum system efficacy of 100 lumen/watt (Similar to Philips Catalogue no. LL199X 1XDLED40-6500 PSE OD WH or equivalent). The luminaire shall have a extrusion housing and light emitted shall have a CRI>80 with rated system lifetime of 50,000 hours at L70. The extrusion housing shall be available in 4', 8' and 12' sections. (Platform Public Area) | NO | 116
F | Supply, installation, testing and commissioning of surface mounted LED Batten - 38 Watt (Similar to Philips Catalogue no. BN 108C LED 40S PSU CDL WH 919515810658 or equivalent), with a system lumen output of 4000 lumens and a minimum system efficacy of 100 lumen/watt. The luminaire shall have a CRI of greater than 80 with rated system lifetime of 50,000 hours at L70. The luminaire is made of CRCA housing and shall have diffused optics. (BOH without False Ceiling Area) | NO
F | Mirror Optic Recess mounted luminaries (Similar to Philips catalogue.No TCS 255 / 2x28 OR Keselec equivalent subject to approval by ER, Catalog no Pharma (Sym/Asym) 2x28 ) with housing made of white powder coated CRCA sheet steel, accommodating all electrical accessories pre-wired upto a terminal block. It should have high efficiency mirror optic anodised aluminium reflector for symmetrical and asymmetrical light distribution and must conform to Ingress Protection Classification of IP 54 (for dust and moisture protection). The luminaries should be suitable for 2 x 28W Tubular Flourescent Lamps and supplied with 2 Nos 28W Tubular Flourescent Lamps. | NO
H | Supply of Integral LED 4 ftwaterproof luminaire with UV Shielded polycarbonate housing and openable end caps. The luminaire should have a color consistency SDCM < 5, CRI > 80 and CCT of 6500K. The luminaire shall be compliant with IP65 and IK08 classification. Luminaire shall be designed to emit at least 4400 nominal lumens with maximum system wattage of 20 watts at a system efficacy of atleast 120 lumen/watt. The luminaire shall be designed so as to ensure lumen depreciation of up to 30% over 50k burning hours @ design ambient temp 45 deg C. Luminaire to be flickerfree with ripple <5%.The electronic driver used shall have a power factor >0.95 and THD <10% and suitable for an operationg voltage range of 140-270V ACThe electronic driver used shall have a power factor >0.95 and THD <10% and has high low cutoff with auto restart suitable for an operationg voltage range of 140-270V AC with high voltage cut off at 325. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters.Similar to WT201C LED44S-6500 PSU L120 S2(UNDERCROFT AREA) | NO | 173
I | Supply of LED Bulkhead with pressure die cast aluminium housing and PC diffuser. The fixture should have CRI > 80 and CCT of both 6500K. The luminaire shall be compliant with IP65 and IK08 classification. Luminaire shall be designed to emit at least 700 nominal lumens and maximum system wattage of 6.5 Watts. T.The luminaire shall be designed so as to ensure lumen depreciation of up to 30% over 25k burning hours @ design ambient temp 45 deg C. The electronic driver used shall have a power factor >0.9 and THD <20% . Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Similar to WT140W LED7S CW PSU S1 PC.(Shaft Area) | NO | 10
J | RC 780P Corridor Fixture | NO | 119
K | Supply of LED based Flood light, housing made up of pressure die cast aluminum Alloy with effective thermal management,sturdiness and embossed brand name/logo name of manufacturer. The fixture should have a minimum system efficacy of 110 lumen/Watt and a minimum system lumen output of 13500 lumens and maximum system wattage of 120 Watts.The fixture shall have a CRI of minimum 70. The fixture shall be designed for a system life of 50,000 hours @70% lumen maintenance. Ingress Protection of IP66 (lamp and gear Compartment) and Mechanical Impact Resistance Rating of IK >=05.The fixture driver should have an operating voltage range of 140-270 V with autocut off at 325V, surge protection of >=3KV, PF >0.9 and THD<20%. The fixture should comply with the parameters as per IS10322. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Similar to Philips CAT No. -BVP122 LED135 CW HE NB FG XTFC | NO | 9
L | Mirror Optic, recessed mounted Luminaries (Similar to Philips catalogue.No TBS/TCS 255 / 228 OR Keselec Catalog no.Pharma 2x28HF) with housing made of white powder coated CRCA Sheet Steel, accomodating all electrical accessories pre-wired upto a terminal box. It should have high efficiency mirror optic anodised aluminium reflector and must conform to Ingress Protection Classification of IP 54 (for dust and moisture Protection). The Luminaries should be suitable for 2 x 28W Tubular Flourescent lamp and supplied with 2 Nos. 28W Tubular Flourescent Lamp. | NO | 445
M | Supply of Mirror Optic, Surface mounted Luminaries (Similar to Philips catalogue No. TCS 399 / 228 OR Keselec Catalog no. Airolux DL 2/28W HF) or equivelent as per approved list, with housing made of powder coated CRCA Sheet Steel, accomodating all electrical accessories . It should have high efficiency mirror optic reflector . The Luminaries should be suitable for 2 x 36W Tubular Flourescent lamp and supplied with 2 Nos. 36W Tubular Flourescent Lamp. | NO | 360
N | Mirror Optic Recess mounted luminaries (Similar to Philips catalogue.No TBS 669 / 128 D6 OR Keselec Catalog no.CT lux DL 1x28HF) with housing made of white powder coated CRCA sheet steel, accommodating all electrical accessories pre-wired upto a terminal block. It should have high efficiency mirror optic reflector of high quality aluminium with parabolic side reflector, 3D cross lamallae with fresnell top and concave lower contour. The luminaries should be suitable for 1 x 28W Tubular Flourescent Lamps and supplied with 1 Nos 28W Tubular Flourescent Lamps. | NO | 10
O | Tunnel luminaire with high impact resistance IK10, IP-65 weather proof type, industrail LED type with housing and fire resistant low smoke halogen free type and non combustible materials (suitable for loop in & loop out with 4x4 sq mm/4x2.5 sq mm cable). similar to Phillips Cat BWP 120 LED 16 CWPC S1, as per specifications. | NO | 180
5.2 | Supply, Installation,Testing and Commission of Separate set of Nickel Cadmium battery with battery charger compatibles with all types of fixture mentioned above except Metal Halide & Flood Light type of fixtures with 2 hours back-up. | NO | 445

## SHC
Hutatma Chowk Station
|  | Units | Quantity | Price | Total Price
5 | INDOOR LIGHTING
The Lighting System specified herein, must conform to Specifications, in addtion to the description given in respective items of BOQ, whether explicitly specified or not. In case of contradiction between specifications and description in BOQ, the most stringent of the condition will prevail.
All the items / parts mentioned in relevant clauses of the specifications and not specifically mentioned in BOQ shall be deemed to be included in the quoted rates, unless specifically excluded.
5.1 | Supply, Installation, Testing and Commissioning of the following Luminaires including all accessories and all fixing accessories shall be as per Specification.
All wiring within the luminarries must be with Fire Resistant LSZH Wires, as per requirements of Specifications.
A | General purpose, basic batten luminaries (Similar to Philips catalogue No. TMS 122, 2x28 T5 OR Keselec Catalog no.Railux 2x28 HF) for 'TL'D fluorescent lamp with - Surface mounting arrangement on wall or ceiling - Single piece channel construction made of powder coated CRCA white sheet steel - Lamp holder brackets and HF electronics ballast. The luminaries should be suitable for 2 x 28W Tubular Flourescent Lamp and supplied with 2 Nos 28W Tubular Flourescent lamps. | NO | 250
B | General purpose, basic batten luminaries (Similar to Philips catalogue.No. TMC 122, 1x28 OR Keselec Catalog no Railux 1x28HF) for 'TL'D fluorescent lamp with - Surface mounting arrangement on wall or ceiling - Single piece channel construction made of powder coated CRCA white sheet steel - Lamp holder brackets and HF electronics ballast. The luminaries should be suitable for 1x28W Tubular Flourescent Lamp and supplied with 1 No. 28W Tubular Flourescent lamps. | NO | 30
C | General purpose basic batten luminaries (Similar to Philips catalogue.No. TMS 122, 2x28W OR Keselec Catalog no. Indilux V 228 HF with vitreous enamelled reflector) for 'TL'D fluorescent lamp with - Surface mounting arrangement on wall or ceiling - Single piece channel construction made of powder coated CRCA white sheet steel - Vitreous Enamelled Reflector of white colour - Lamp holder brackets and HF electronics ballast. The luminaries should be suitable for 2x28W Tubular Flourescent lamp and supplied with 2 Nos 28W Tubular Flourescent lamps. | NO | 480
D | Mirror Optic Recess mounted luminaries (Similar to Bajaj catalogue.No BTMRA 4x14 OR Philips OR Keselec equivalent subject to approval by ER | NO | 50
E | Efficient, low glare, surface mounted luminaries (Similar to Philips Catalogue No. MPF 922 / 1 X 70W) with integral gear, electrochemically brightened and anodized high purity aluminium reflector of symmetrical type. The luminaries must be non corrosive pressure die cast aluminium housing and white powder coated finish and must be suitable for ceiling mounting. It should have cover made of heat resistant toughened glass and the must be conforming to Ingress Protection Classification of IP 65 (for dust and moisture protection). The luminaries should be suitable for, and supplied with, One No 70W Metal Halide lamp . | NO | 50
F | Mirror Optic Recess mounted luminaries (Similar to Philips catalogue.No TBS 669 / 228 D6 OR Keselec Catalog no.CT lux 2x28HF) with housing made of white powder coated CRCA sheet steel, accommodating all electrical accessories pre-wired upto a terminal block. It should have high efficiency mirror optic reflector of high quality aluminium with parabolic side reflector, 3D cross lamallae with fresnell top and concave lower contour. The luminaries should be suitable for 2 x 28W Tubular Flourescent Lamps and supplied with 2 Nos 28W Tubular Flourescent Lamps. | NO | 135
F | Mirror Optic Recess mounted luminaries (Similar to Philips catalogue.No TCS 255 / 2x28 OR Keselec equivalent subject to approval by ER, Catalog no Pharma (Sym/Asym) 2x28 ) with housing made of white powder coated CRCA sheet steel, accommodating all electrical accessories pre-wired upto a terminal block. It should have high efficiency mirror optic anodised aluminium reflector for symmetrical and asymmetrical light distribution and must conform to Ingress Protection Classification of IP 54 (for dust and moisture protection). The luminaries should be suitable for 2 x 28W Tubular Flourescent Lamps and supplied with 2 Nos 28W Tubular Flourescent Lamps. | NO | 280
H | General purpose basic batten luminaries (Similar to Philips catalogue.No. TCW 450, 1x28 OR Keselec Catalog no.Railux 1x28 HF) for 'TL'D fluorescent lamp with - Surface mounting arrangement on wall or ceiling - Single piece channel construction made of powder coated CRCA white sheet steel - Lamp holder brackets and HF electronics ballast - Wire Guard to protect the lamp The luminaries should be suitable for 1 x 28W Tubular Flourescent lamp and supplied with 1 Nos 28W Tubular Flourescent lamps. | NO | 220
I | Recessed Circular Down Light luminaries (Similar to Philips catalogue.No FBH 145 / 218 OR Keselec Catalog no.Nova 2x18 (G)) with satin finished, anodised aluminium reflector and clear glass cover. The luminaries should be suitable for 2 x 18 W CFL lamps and supplied with 2 Nos 18W CFL lamps. | NO | 55
J | Mirror Optic, recessed mounted Luminaries (Similar to Philips catalogue.No TBS/TCS 255 / 228 OR Keselec Catalog no.Pharma 2x28HF) with housing made of white powder coated CRCA Sheet Steel, accomodating all electrical accessories pre-wired upto a terminal box. It should have high efficiency mirror optic anodised aluminium reflector and must conform to Ingress Protection Classification of IP 54 (for dust and moisture Protection). The Luminaries should be suitable for 2 x 28W Tubular Flourescent lamp and supplied with 2 Nos. 28W Tubular Flourescent Lamp. | NO | 80
K | Supply of Mirror Optic, Surface mounted Luminaries (Similar to Philips catalogue No. TCS 399 / 228 OR Keselec Catalog no. Airolux DL 2/28W HF) or equivelent as per approved list, with housing made of powder coated CRCA Sheet Steel, accomodating all electrical accessories . It should have high efficiency mirror optic reflector . The Luminaries should be suitable for 2 x 36W Tubular Flourescent lamp and supplied with 2 Nos. 36W Tubular Flourescent Lamp. | NO | 735
L | Mirror Optic Recess mounted luminaries (Similar to Philips catalogue.No TBS 669 / 128 D6 OR Keselec Catalog no.CT lux DL 1x28HF) with housing made of white powder coated CRCA sheet steel, accommodating all electrical accessories pre-wired upto a terminal block. It should have high efficiency mirror optic reflector of high quality aluminium with parabolic side reflector, 3D cross lamallae with fresnell top and concave lower contour. The luminaries should be suitable for 1 x 28W Tubular Flourescent Lamps and supplied with 1 Nos 28W Tubular Flourescent Lamps. | NO | 10
N | Tunnel luminaire with high impact resistance IK10, IP-65 weather proof type, industrail LED type with housing and fire resistant low smoke halogen free type and non combustible materials (suitable for loop in & loop out with 4x4 sq mm/4x2.5 sq mm cable). similar to Phillips Cat BWP 120 LED 16 CWPC S1, as per specifications. | NO | 235
O | Bulk Head luminaries (Similar to Philips Catalogue No FXC 101 OR Keselec Catalog no. KBH 1x9 W) suitable for mounting on wall / ceiling having -Single piece pressure die cast Aluminium housing - Wire Guard made of powder coated MS - Heat resistant Glass cover The luminaries must conform to Ingress Protection Classification of IP 54 (for dust and Moisture Protection ). The luminaries should be suitable for 1 x 9W CFL lamp and supplied with 1 No. 9W CFL lamp and control accessories. | NO | 25
Q | Surface/Suspended type moisture proof diffuser luminiare with housing made of grey, high impact resistant polycarbonate, with Non-ageing gasket consisting of 2-component polyurethane foam. Difuser made of one piece injection moulded high impact resistant polycarbonate also computer optimised internal prismatic structure for precise direction of light and glare reduction, with difuser clips made of stainless steel, roll formed galvanised steel reflector that is enamelled white and can be suspended from either side of the housing. Suitable for 2x28W FTL Lamp prewired upto a terminal box with lamp. Having IP 65 (similar to Philips catalogue No. TCW 450 \ 2 x 28W HF or Keselec make sub 2x28W HF) and supplied with 2 Nos 28W Tubular Flourescent Lamps. | NO | 10
FL-1 | Compact, sturdy, general purpose floodlight luminaries (Similar to Philips catalogue. No TEMPO3 SWF 330 SK type OR Keselec make KSFL/250W/ SON-T) with integral gear, electrochemically brightened and anodized high purity aluminium reflector of symmetrical type. The luminaries must be adjustable with rugged, non corrosive pressure die cast aluminium housing and black powder coated finish and must be suitable for column mounting. It should have cover made of heat resistant toughened glass and the must be conforming to Ingress Protection Classification of IP 65 (for dust and moisture protection). The luminaries should be suitable for, and supplied with, One No 250W Sodium Vapour lamp. | NO | 20
FL-2 | Compact, sturdy, general purpose floodlight luminaries (Similar to Philips catalogue. No TEMPO3 MWF 330\250 AK HPI -T PLUS lamp OR Keselec make KSFL 250W/ HPI-T Plus) with integral gear, electrochemically brightened and anodized high purity aluminium reflector of symmetrical type. The luminaries must be adjustable with rugged, non corrosive pressure die cast aluminium housing and black powder coated finish and must be suitable for column mounting. It should have cover made of heat resistant toughened glass and the must be conforming to Ingress Protection Classification of IP 65 (for dust and moisture protection). The luminaries should be suitable for, and supplied with, One No 250W Metal halide lamp.(For double height area) | NO | 10
5.2 | Supply, Installation,Testing and Commission of Separate set of Nickel Cadmium battery with battery charger compatibles with all types of fixture mentioned above except Metal Halide & Flood Light type of fixtures with 2 hours back-up. | NO | 443
5.6 | External station Lighting
5.6.1 | Supply,Installation,testing and Commisioning of Hot dip galvanised Octagonal poles similar to -Bajaj Make cat ref. BOP-1040 height 10 mtr ,top dia 100mm,Bottom dia 200mm,plate thickness 4 MM, Base plate 310x310x20 mm foundation PCD 310 mm size 4x25mm dia ,space for cable termination block at the top half of the polewith cover plate | No | 10
5.6.2 | Supply ,Installation,Testing and commisioning of 1x250W HPSV MH-T(Die cast aluminium top ,maintanable street light luminarie with curved toughened glass 7 pot optic reflector with IP 66 Lamp Compartment.Complete.Similar to 338/250W ( similar to Velocity model of Phillips make) | No | 10
a | Supply,Testing and Installation of 250 W HPSV Lamp (Phillips/Osram Make) | No | 5
b | Supply,Testing and Installation of 250 W Metal halide Lamp (Phillips/Osram Make) | No | 5
5.6.3 | Supply of 75mm dia HDPE pipe confirming to PN-4 boring of road channel area by using open trench method and laying of HDPE pipe properly continuously jointed restoring the surface where pitting is done ,to original position. | Mtr | 15
5.6.4 | Supply of 75mm dia HDPE pipe confirming to PN-4 boring of road channel area by using trench less method and laying of HDPE pipe properly continuously jointed restoring the surface where pitting is done ,to original position. | Mtr | 15
5.6.5 | Supply and installation of GI Bracket single arm,painted, 1m over hang. | No | 15
5.6.6 | Supply and installation of GI Bracketdouble arm,painted 1m over hang | No | 5
5.6.7 | Supply and installation of GI Bracket Tripple arm,painted,1m over hang | No | 5
5.6.8 | Supply and laying of 6 SWG wire along with the cable | Mtr | 50
5.6.9 | Providing and fixing thermo plastic poly carbonate pole boxex confirming to IP-65 degree of protection, along with 16A MCB and 5 way connector and 2 No. cable gland suitable for 4x25 sq.mm cable. | each | 15
5.6.10 | Assembly of pre supplied fitting parts such as choke, bulb, igniter etc ready for energisation and installation of the same on single / double/ tripple GI bracket, fixing of nuts and bolts properly with the help of tower wagon ( Tower wagon shall be arranged by the contractor at his own cost.) | each | 25
5.6.11 | wiring for lumanaries in existing poles with following sizes of unarmoured cu cables from ploe box to each fittings.
| 3x2.5 sq mm | Mtr | 50

## shc revised
Hutatma Chowk Station Revised
|  | Units | Quantity | Price | Total Price
5 | INDOOR LIGHTING
The Lighting System specified herein, must confirm to Specifications, in addtion to the description given in respective items of BOQ, whether explicitly specified or not. In case of contradiction between specifications and description in BOQ, the most stringent of the condition will prevail.
All the items / parts mentioned in relevant clauses of the specifications and not specifically mentioned in BOQ shall be deemed to be included in the quoted rates, unless specifically excluded.
5.1 | Supply, Installation, Testing and Commissioning of the following Luminaires including all accessories and all fixing accessories shall be as per Specification.
All wiring within the luminarries must be with Fire Resistant LSZH Wires, as per requirements of Specifications.
A | Supply of LED 2x2 luminaire with CRCA housing suitable with fully diffused diffuser for general lighting in office areas. The luminaire should have a color consistency SDCM < 5, CRI > 80 and CCT of 6500K. The luminaire shall be compliant with IP20 and IK02 classification. Luminaire shall be designed to emit at least 3600 nominal lumens and an outstanding backlit solution efficacy of atleast 115 lumen/watt and maximum system wattage of 31 Watts. The lumanaire should have outstanding backlit solution efficacy.The luminaire shall be designed so as to ensure lumen depreciation of up to 30% over 50k burning hours @ design ambient temp 45 deg C. The electronic driver used shall have a power factor >0.95 and THD <10% and have options for DALI dimmable too. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Similar to RC380B LED36S -6500 G4 L60 W60 PSU OD. (BOH with False Ceiling Area) | NO | 40
B | Supply of Integral LED 4 ft luminaire with CRCA housing and UV shielded PC Glossy cover. The luminaire should have a color consistency SDCM < 5, CRI > 80 and CCT of 6500K. The luminaire shall be compliant with IP20 classification. Luminaire shall be designed to emit at least 4000 nominal lumens with maximum system wattage of 34 watts at a system efficacy of atleast 120 lumen/watt. The luminaire shall be designed so as to ensure lumen depreciation of up to 30% over 50k burning hours @ design ambient temp 45 deg C. Luminaire to be flickerfree with ripple <5%. The electronic driver used shall have a power factor >0.95 and THD <10% and has high low cutoff with auto restart suitable for an operationg voltage range of 140-270V AC with high voltage cut of 325V. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters.Similar to BN308C LED40S-6500 L120 PSU WH. (BOH without False Ceiling Area) | NO | 435
| Supply of Integral LED 4 ft luminaire with CRCA housing and UV shielded PC Glossy cover. The luminaire should have a color consistency SDCM < 5, CRI > 80 and CCT of 6500K. The luminaire shall be compliant with IP20 classification. Luminaire shall be designed to emit at least 2000 nominal lumens with maximum system wattage of 16 watts at a system efficacy of atleast 120 lumen/watt. The luminaire shall be designed so as to ensure lumen depreciation of up to 30% over 50k burning hours @ design ambient temp 45 deg C. Luminaire to be flickerfree with ripple <5%. The electronic driver used shall have a power factor >0.95 and THD <10% and has high low cutoff with auto restart suitable for an operationg voltage range of 140-270V AC with high voltage cut off at 325V. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters.Similar to BN308C LED20S-6500 L120 PSU WH. |  | 85
C | Supply of LED recessed downlighter with pressure die cast alumium housing . The luminaire should have a color consistency SDCM < 5, CRI > 80 and CCT of 6500K. The luminaire shall be compliant with IP20 and IK02 classification. Luminaire shall be designed to emit at least 1500 system lumens with maximum system wattage of 13.5 Watts. The lumanaire should have outstanding backlit solution efficacy.The luminaire shall be designed so as to ensure lumen depreciation of up to 30% over 50k burning hours @ design ambient temp 45 deg C. The electronic driver used shall have a power factor >0.95 and THD <10% and have operating voltage range from 130-320V. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Similar to DN296B LED15S-6500 PSU WH (Toilets) | NO | 25
D | Supply, installation, testing and commissioning of LED Linear 1x4 recessed fixture - 42 Watt, with a system lumen output of 3000 lumens at an efficacy of >65 lm/W (Similar to Philips Catalogue no. RC869 B W30 L120 LED or equivalent). The luminaire shall have powder coated CRCA housing and light output is by means of Semi High Gloss optics with 3D Lamellae and High Purity Anodized Aluminium mirrors. (Concourse & Platform Public Area) | NO | 790
E | Supply, installation, testing and commissioning of LED trunking system - 40 Watt , with a system lumen output of 4000 lumens and a minimum system efficacy of 100 lumen/watt (Similar to Philips Catalogue no. LL199X 1XDLED40-6500 PSE OD WH or equivalent). The luminaire shall have a extrusion housing and light emitted shall have a CRI>80 with rated system lifetime of 50,000 hours at L70. The extrusion housing shall be available in 4', 8' and 12' sections. (Platform Public Area) | NO | 130
F | Supply, installation, testing and commissioning of surface mounted LED Batten - 38 Watt (Similar to Philips Catalogue no. BN 108C LED 40S PSU CDL WH 919515810658 or equivalent), with a system lumen output of 4000 lumens and a minimum system efficacy of 100 lumen/watt. The luminaire shall have a CRI of greater than 80 with rated system lifetime of 50,000 hours at L70. The luminaire is made of CRCA housing and shall have diffused optics. (BOH without False Ceiling Area) | NO | 120
F | Mirror Optic Recess mounted luminaries (Similar to Philips catalogue.No TCS 255 / 2x28 OR Keselec equivalent subject to approval by ER, Catalog no Pharma (Sym/Asym) 2x28 ) with housing made of white powder coated CRCA sheet steel, accommodating all electrical accessories pre-wired upto a terminal block. It should have high efficiency mirror optic anodised aluminium reflector for symmetrical and asymmetrical light distribution and must conform to Ingress Protection Classification of IP 54 (for dust and moisture protection). The luminaries should be suitable for 2 x 28W Tubular Flourescent Lamps and supplied with 2 Nos 28W Tubular Flourescent Lamps. | NO | 280
H | Supply of Integral LED 4 ftwaterproof luminaire with UV Shielded polycarbonate housing and openable end caps. The luminaire should have a color consistency SDCM < 5, CRI > 80 and CCT of 6500K. The luminaire shall be compliant with IP65 and IK08 classification. Luminaire shall be designed to emit at least 4400 nominal lumens with maximum system wattage of 20 watts at a system efficacy of atleast 120 lumen/watt. The luminaire shall be designed so as to ensure lumen depreciation of up to 30% over 50k burning hours @ design ambient temp 45 deg C. Luminaire to be flickerfree with ripple <5%.The electronic driver used shall have a power factor >0.95 and THD <10% and suitable for an operationg voltage range of 140-270V ACThe electronic driver used shall have a power factor >0.95 and THD <10% and has high low cutoff with auto restart suitable for an operationg voltage range of 140-270V AC with high voltage cut off at 325. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters.Similar to WT201C LED44S-6500 PSU L120 S2(UNDERCROFT AREA) | NO | 170
I | Supply of LED Bulkhead with pressure die cast aluminium housing and PC diffuser. The fixture should have CRI > 80 and CCT of both 6500K. The luminaire shall be compliant with IP65 and IK08 classification. Luminaire shall be designed to emit at least 700 nominal lumens and maximum system wattage of 6.5 Watts. T.The luminaire shall be designed so as to ensure lumen depreciation of up to 30% over 25k burning hours @ design ambient temp 45 deg C. The electronic driver used shall have a power factor >0.9 and THD <20% . Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Similar to WT140W LED7S CW PSU S1 PC.(Shaft Area) | NO | 10
| Supply of LED fixture similar to Philips RC 780 24W. The fixture should have CRI > 80 and CCT of both 6500K. | NO | 171
J | Mirror Optic, recessed mounted Luminaries (Similar to Philips catalogue.No TBS/TCS 255 / 228 OR Keselec Catalog no.Pharma 2x28HF) with housing made of white powder coated CRCA Sheet Steel, accomodating all electrical accessories pre-wired upto a terminal box. It should have high efficiency mirror optic anodised aluminium reflector and must conform to Ingress Protection Classification of IP 54 (for dust and moisture Protection). The Luminaries should be suitable for 2 x 28W Tubular Flourescent lamp and supplied with 2 Nos. 28W Tubular Flourescent Lamp. | NO | 445
K | Supply of Mirror Optic, Surface mounted Luminaries (Similar to Philips catalogue No. TCS 399 / 228 OR Keselec Catalog no. Airolux DL 2/28W HF) or equivelent as per approved list, with housing made of powder coated CRCA Sheet Steel, accomodating all electrical accessories . It should have high efficiency mirror optic reflector . The Luminaries should be suitable for 2 x 36W Tubular Flourescent lamp and supplied with 2 Nos. 36W Tubular Flourescent Lamp. | NO | 360
L | Mirror Optic Recess mounted luminaries (Similar to Philips catalogue.No TBS 669 / 128 D6 OR Keselec Catalog no.CT lux DL 1x28HF) with housing made of white powder coated CRCA sheet steel, accommodating all electrical accessories pre-wired upto a terminal block. It should have high efficiency mirror optic reflector of high quality aluminium with parabolic side reflector, 3D cross lamallae with fresnell top and concave lower contour. The luminaries should be suitable for 1 x 28W Tubular Flourescent Lamps and supplied with 1 Nos 28W Tubular Flourescent Lamps. | NO | 10
N | Tunnel luminaire with high impact resistance IK10, IP-65 weather proof type, industrail LED type with housing and fire resistant low smoke halogen free type and non combustible materials (suitable for loop in & loop out with 4x4 sq mm/4x2.5 sq mm cable). similar to Phillips Cat BWP 120 LED 16 CWPC S1, as per specifications. | NO | 263
O | Bulk Head luminaries (Similar to Philips Catalogue No FXC 101 OR Keselec Catalog no. KBH 1x9 W) suitable for mounting on wall / ceiling having -Single piece pressure die cast Aluminium housing - Wire Guard made of powder coated MS - Heat resistant Glass cover The luminaries must conform to Ingress Protection Classification of IP 54 (for dust and Moisture Protection ). The luminaries should be suitable for 1 x 9W CFL lamp and supplied with 1 No. 9W CFL lamp and control accessories. | NO | 25
Q | Surface/Suspended type moisture proof diffuser luminiare with housing made of grey, high impact resistant polycarbonate, with Non-ageing gasket consisting of 2-component polyurethane foam. Difuser made of one piece injection moulded high impact resistant polycarbonate also computer optimised internal prismatic structure for precise direction of light and glare reduction, with difuser clips made of stainless steel, roll formed galvanised steel reflector that is enamelled white and can be suspended from either side of the housing. Suitable for 2x28W FTL Lamp prewired upto a terminal box with lamp. Having IP 65 (similar to Philips catalogue No. TCW 450 \ 2 x 28W HF or Keselec make sub 2x28W HF) and supplied with 2 Nos 28W Tubular Flourescent Lamps. | NO | 10
FL-1 | Compact, sturdy, general purpose floodlight luminaries (Similar to Philips catalogue. No TEMPO3 SWF 330 SK type OR Keselec make KSFL/250W/ SON-T) with integral gear, electrochemically brightened and anodized high purity aluminium reflector of symmetrical type. The luminaries must be adjustable with rugged, non corrosive pressure die cast aluminium housing and black powder coated finish and must be suitable for column mounting. It should have cover made of heat resistant toughened glass and the must be conforming to Ingress Protection Classification of IP 65 (for dust and moisture protection). The luminaries should be suitable for, and supplied with, One No 250W Sodium Vapour lamp. | NO | 20
FL-2 | Compact, sturdy, general purpose floodlight luminaries (Similar to Philips catalogue. No TEMPO3 MWF 330\250 AK HPI -T PLUS lamp OR Keselec make KSFL 250W/ HPI-T Plus) with integral gear, electrochemically brightened and anodized high purity aluminium reflector of symmetrical type. The luminaries must be adjustable with rugged, non corrosive pressure die cast aluminium housing and black powder coated finish and must be suitable for column mounting. It should have cover made of heat resistant toughened glass and the must be conforming to Ingress Protection Classification of IP 65 (for dust and moisture protection). The luminaries should be suitable for, and supplied with, One No 250W Metal halide lamp.(For double height area) | NO | 10
5.2 | Supply, Installation,Testing and Commission of Separate set of Nickel Cadmium battery with battery charger compatibles with all types of fixture mentioned above except Metal Halide & Flood Light type of fixtures with 2 hours back-up. | NO | 445

## SVB
Vidhan Bhavan station
|  | Units | Quantity | Price | Total Price
5 | INDOOR LIGHTING
The Lighting System specified herein, must confirm to Specifications, in addtion to the description given in respective items of BOQ, whether explicitly specified or not. In case of contradiction between specifications and description in BOQ, the most stringent of the condition will prevail.
All the items / parts mentioned in relevant clauses of the specifications and not specifically mentioned in BOQ shall be deemed to be included in the quoted rates, unless specifically excluded.
5.1 | Supply, Installation, Testing and Commissioning of the following Luminaires including all accessories and all fixing accessories shall be as per Specification.
All wiring within the luminarries must be with Fire Resistant LSZH Wires, as per requirements of Specifications.
A | General purpose, basic batten luminaries (Similar to Philips catalogue No. TMS 122, 2x28 T5 OR Keselec Catalog no.Railux 2x28 HF) for 'TL'D fluorescent lamp with - Surface mounting arrangement on wall or ceiling - Single piece channel construction made of powder coated CRCA white sheet steel - Lamp holder brackets and HF electronics ballast. The luminaries should be suitable for 2 x 28W Tubular Flourescent Lamp and supplied with 2 Nos 28W Tubular Flourescent lamps. | NO | 65
B | General purpose, basic batten luminaries (Similar to Philips catalogue.No. TMC 122, 1x28 OR Keselec Catalog no Railux 1x28HF) for 'TL'D fluorescent lamp with - Surface mounting arrangement on wall or ceiling - Single piece channel construction made of powder coated CRCA white sheet steel - Lamp holder brackets and HF electronics ballast. The luminaries should be suitable for 1x28W Tubular Flourescent Lamp and supplied with 1 No. 28W Tubular Flourescent lamps. | NO | 125
C | General purpose basic batten luminaries (Similar to Philips catalogue.No. TMS 122, 2x28W OR Keselec Catalog no. Indilux V 228 HF with vitreous enamelled reflector) for 'TL'D fluorescent lamp with - Surface mounting arrangement on wall or ceiling - Single piece channel construction made of powder coated CRCA white sheet steel - Vitreous Enamelled Reflector of white colour - Lamp holder brackets and HF electronics ballast. The luminaries should be suitable for 2x28W Tubular Flourescent lamp and supplied with 2 Nos 28W Tubular Flourescent lamps. | NO | 374
D | Mirror Optic Recess mounted luminaries (Similar to Bajaj catalogue.No BTMRA 4x14 OR Philips OR Keselec equivalent subject to approval by ER | NO | 28
E | Efficient, low glare, surface mounted luminaries (Similar to Philips Catalogue No. MPF 922 / 1 X 70W) with integral gear, electrochemically brightened and anodized high purity aluminium reflector of symmetrical type. The luminaries must be non corrosive pressure die cast aluminium housing and white powder coated finish and must be suitable for ceiling mounting. It should have cover made of heat resistant toughened glass and the must be conforming to Ingress Protection Classification of IP 65 (for dust and moisture protection). The luminaries should be suitable for, and supplied with, One No 70W Metal Halide lamp . | NO | 50
F | Mirror Optic Recess mounted luminaries (Similar to Philips catalogue.No TBS 669 / 228 D6 OR Keselec Catalog no.CT lux 2x28HF) with housing made of white powder coated CRCA sheet steel, accommodating all electrical accessories pre-wired upto a terminal block. It should have high efficiency mirror optic reflector of high quality aluminium with parabolic side reflector, 3D cross lamallae with fresnell top and concave lower contour. The luminaries should be suitable for 2 x 28W Tubular Flourescent Lamps and supplied with 2 Nos 28W Tubular Flourescent Lamps. | NO | 120
F | Mirror Optic Recess mounted luminaries (Similar to Philips catalogue.No TCS 255 / 2x28 OR Keselec equivalent subject to approval by ER, Catalog no Pharma (Sym/Asym) 2x28 ) with housing made of white powder coated CRCA sheet steel, accommodating all electrical accessories pre-wired upto a terminal block. It should have high efficiency mirror optic anodised aluminium reflector for symmetrical and asymmetrical light distribution and must conform to Ingress Protection Classification of IP 54 (for dust and moisture protection). The luminaries should be suitable for 2 x 28W Tubular Flourescent Lamps and supplied with 2 Nos 28W Tubular Flourescent Lamps. | NO | 280
H | General purpose basic batten luminaries (Similar to Philips catalogue.No. TCW 450, 1x28 OR Keselec Catalog no.Railux 1x28 HF) for 'TL'D fluorescent lamp with - Surface mounting arrangement on wall or ceiling - Single piece channel construction made of powder coated CRCA white sheet steel - Lamp holder brackets and HF electronics ballast - Wire Guard to protect the lamp The luminaries should be suitable for 1 x 28W Tubular Flourescent lamp and supplied with 1 Nos 28W Tubular Flourescent lamps. | NO | 145
I | Recessed Circular Down Light luminaries (Similar to Philips catalogue.No FBH 145 / 218 OR Keselec Catalog no.Nova 2x18 (G)) with satin finished, anodised aluminium reflector and clear glass cover. The luminaries should be suitable for 2 x 18 W CFL lamps and supplied with 2 Nos 18W CFL lamps. | NO | 45
J | Mirror Optic, recessed mounted Luminaries (Similar to Philips catalogue.No TBS/TCS 255 / 228 OR Keselec Catalog no.Pharma 2x28HF) with housing made of white powder coated CRCA Sheet Steel, accomodating all electrical accessories pre-wired upto a terminal box. It should have high efficiency mirror optic anodised aluminium reflector and must conform to Ingress Protection Classification of IP 54 (for dust and moisture Protection). The Luminaries should be suitable for 2 x 28W Tubular Flourescent lamp and supplied with 2 Nos. 28W Tubular Flourescent Lamp. | NO | 445
K | Supply of Mirror Optic, Surface mounted Luminaries (Similar to Philips catalogue No. TCS 399 / 228 OR Keselec Catalog no. Airolux DL 2/28W HF) or equivelent as per approved list, with housing made of powder coated CRCA Sheet Steel, accomodating all electrical accessories . It should have high efficiency mirror optic reflector . The Luminaries should be suitable for 2 x 36W Tubular Flourescent lamp and supplied with 2 Nos. 36W Tubular Flourescent Lamp. | NO | 360
L | Mirror Optic Recess mounted luminaries (Similar to Philips catalogue.No TBS 669 / 128 D6 OR Keselec Catalog no.CT lux DL 1x28HF) with housing made of white powder coated CRCA sheet steel, accommodating all electrical accessories pre-wired upto a terminal block. It should have high efficiency mirror optic reflector of high quality aluminium with parabolic side reflector, 3D cross lamallae with fresnell top and concave lower contour. The luminaries should be suitable for 1 x 28W Tubular Flourescent Lamps and supplied with 1 Nos 28W Tubular Flourescent Lamps. | NO | 10
N | Tunnel luminaire with high impact resistance IK10, IP-65 weather proof type, industrail LED type with housing and fire resistant low smoke halogen free type and non combustible materials (suitable for loop in & loop out with 4x4 sq mm/4x2.5 sq mm cable). similar to Phillips Cat BWP 120 LED 16 CWPC S1, as per specifications. | NO | 210
O | Bulk Head luminaries (Similar to Philips Catalogue No FXC 101 OR Keselec Catalog no. KBH 1x9 W) suitable for mounting on wall / ceiling having -Single piece pressure die cast Aluminium housing - Wire Guard made of powder coated MS - Heat resistant Glass cover The luminaries must conform to Ingress Protection Classification of IP 54 (for dust and Moisture Protection ). The luminaries should be suitable for 1 x 9W CFL lamp and supplied with 1 No. 9W CFL lamp and control accessories. | NO | 25
Q | Surface/Suspended type moisture proof diffuser luminiare with housing made of grey, high impact resistant polycarbonate, with Non-ageing gasket consisting of 2-component polyurethane foam. Difuser made of one piece injection moulded high impact resistant polycarbonate also computer optimised internal prismatic structure for precise direction of light and glare reduction, with difuser clips made of stainless steel, roll formed galvanised steel reflector that is enamelled white and can be suspended from either side of the housing. Suitable for 2x28W FTL Lamp prewired upto a terminal box with lamp. Having IP 65 (similar to Philips catalogue No. TCW 450 \ 2 x 28W HF or Keselec make sub 2x28W HF) and supplied with 2 Nos 28W Tubular Flourescent Lamps. | NO | 10
FL-1 | Compact, sturdy, general purpose floodlight luminaries (Similar to Philips catalogue. No TEMPO3 SWF 330 SK type OR Keselec make KSFL/250W/ SON-T) with integral gear, electrochemically brightened and anodized high purity aluminium reflector of symmetrical type. The luminaries must be adjustable with rugged, non corrosive pressure die cast aluminium housing and black powder coated finish and must be suitable for column mounting. It should have cover made of heat resistant toughened glass and the must be conforming to Ingress Protection Classification of IP 65 (for dust and moisture protection). The luminaries should be suitable for, and supplied with, One No 250W Sodium Vapour lamp. | NO | 20
FL-2 | Compact, sturdy, general purpose floodlight luminaries (Similar to Philips catalogue. No TEMPO3 MWF 330\250 AK HPI -T PLUS lamp OR Keselec make KSFL 250W/ HPI-T Plus) with integral gear, electrochemically brightened and anodized high purity aluminium reflector of symmetrical type. The luminaries must be adjustable with rugged, non corrosive pressure die cast aluminium housing and black powder coated finish and must be suitable for column mounting. It should have cover made of heat resistant toughened glass and the must be conforming to Ingress Protection Classification of IP 65 (for dust and moisture protection). The luminaries should be suitable for, and supplied with, One No 250W Metal halide lamp.(For double height area) | NO | 10
5.2 | Supply, Installation,Testing and Commission of Separate set of Nickel Cadmium battery with battery charger compatibles with all types of fixture mentioned above except Metal Halide & Flood Light type of fixtures with 2 hours back-up. | NO | 445
5.6 | External station Lighting
5.6.1 | Supply,Installation,testing and Commisioning of Hot dip galvanised Octagonal poles similar to -Bajaj Make cat ref. BOP-1040 height 10 mtr ,top dia 100mm,Bottom dia 200mm,plate thickness 4 MM, Base plate 310x310x20 mm foundation PCD 310 mm size 4x25mm dia ,space for cable termination block at the top half of the polewith cover plate | No | 10
5.6.2 | Supply ,Installation,Testing and commisioning of 1x250W HPSV MH-T(Die cast aluminium top ,maintanable street light luminarie with curved toughened glass 7 pot optic reflector with IP 66 Lamp Compartment.Complete.Similar to 338/250W ( similar to Velocity model of Phillips make) | No | 10
a | Supply,Testing and Installation of 250 W HPSV Lamp (Phillips/Osram Make) | No | 5
b | Supply,Testing and Installation of 250 W Metal halide Lamp (Phillips/Osram Make) | No | 5
5.6.3 | Supply of 75mm dia HDPE pipe confirming to PN-4 boring of road channel area by using open trench method and laying of HDPE pipe properly continuously jointed restoring the surface where pitting is done ,to original position. | Mtr | 15
5.6.4 | Supply of 75mm dia HDPE pipe confirming to PN-4 boring of road channel area by using trench less method and laying of HDPE pipe properly continuously jointed restoring the surface where pitting is done ,to original position. | Mtr | 15
5.6.5 | Supply and installation of GI Bracket single arm,painted, 1m over hang. | No | 15
5.6.6 | Supply and installation of GI Bracketdouble arm,painted 1m over hang | No | 5
5.6.7 | Supply and installation of GI Bracket Tripple arm,painted,1m over hang | No | 5
5.6.8 | Supply and laying of 6 SWG wire along with the cable | Mtr | 50
5.6.9 | Providing and fixing thermo plastic poly carbonate pole boxex confirming to IP-65 degree of protection, along with 16A MCB and 5 way connector and 2 No. cable gland suitable for 4x25 sq.mm cable. | each | 15
5.6.10 | Assembly of pre supplied fitting parts such as choke, bulb, igniter etc ready for energisation and installation of the same on single / double/ tripple GI bracket, fixing of nuts and bolts properly with the help of tower wagon ( Tower wagon shall be arranged by the contractor at his own cost.) | each | 25
5.6.11 | wiring for lumanaries in existing poles with following sizes of unarmoured cu cables from ploe box to each fittings.
| 3x2.5 sq mm | Mtr | 50

## SVB Revised
Vidhan Bhavan station Revised
|  | Units | Quantity | Price | Total Price
5 | INDOOR LIGHTING
The Lighting System specified herein, must confirm to Specifications, in addtion to the description given in respective items of BOQ, whether explicitly specified or not. In case of contradiction between specifications and description in BOQ, the most stringent of the condition will prevail.
All the items / parts mentioned in relevant clauses of the specifications and not specifically mentioned in BOQ shall be deemed to be included in the quoted rates, unless specifically excluded.
5.1 | Supply, Installation, Testing and Commissioning of the following Luminaires including all accessories and all fixing accessories shall be as per Specification.
All wiring within the luminarries must be with Fire Resistant LSZH Wires, as per requirements of Specifications.
A | Supply of LED 2x2 luminaire with CRCA housing suitable with fully diffused diffuser for general lighting in office areas. The luminaire should have a color consistency SDCM < 5, CRI > 80 and CCT of 6500K. The luminaire shall be compliant with IP20 and IK02 classification. Luminaire shall be designed to emit at least 3600 nominal lumens and an outstanding backlit solution efficacy of atleast 115 lumen/watt and maximum system wattage of 31 Watts. The lumanaire should have outstanding backlit solution efficacy.The luminaire shall be designed so as to ensure lumen depreciation of up to 30% over 50k burning hours @ design ambient temp 45 deg C. The electronic driver used shall have a power factor >0.95 and THD <10% and have options for DALI dimmable too. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Similar to RC380B LED36S -6500 G4 L60 W60 PSU OD. (BOH with False Ceiling Area) | NO | 28
B | Supply of Integral LED 4 ft luminaire with CRCA housing and UV shielded PC Glossy cover. The luminaire should have a color consistency SDCM < 5, CRI > 80 and CCT of 6500K. The luminaire shall be compliant with IP20 classification. Luminaire shall be designed to emit at least 4000 nominal lumens with maximum system wattage of 34 watts at a system efficacy of atleast 120 lumen/watt. The luminaire shall be designed so as to ensure lumen depreciation of up to 30% over 50k burning hours @ design ambient temp 45 deg C. Luminaire to be flickerfree with ripple <5%. The electronic driver used shall have a power factor >0.95 and THD <10% and has high low cutoff with auto restart suitable for an operationg voltage range of 140-270V AC with high voltage cut of 325V. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters.Similar to BN308C LED40S-6500 L120 PSU WH. (BOH without False Ceiling Area) | NO | 416
| Supply of Integral LED 4 ft luminaire with CRCA housing and UV shielded PC Glossy cover. The luminaire should have a color consistency SDCM < 5, CRI > 80 and CCT of 6500K. The luminaire shall be compliant with IP20 classification. Luminaire shall be designed to emit at least 2000 nominal lumens with maximum system wattage of 16 watts at a system efficacy of atleast 120 lumen/watt. The luminaire shall be designed so as to ensure lumen depreciation of up to 30% over 50k burning hours @ design ambient temp 45 deg C. Luminaire to be flickerfree with ripple <5%. The electronic driver used shall have a power factor >0.95 and THD <10% and has high low cutoff with auto restart suitable for an operationg voltage range of 140-270V AC with high voltage cut off at 325V. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters.Similar to BN308C LED20S-6500 L120 PSU WH. | NO | 61
C | Supply of LED recessed downlighter with pressure die cast alumium housing . The luminaire should have a color consistency SDCM < 5, CRI > 80 and CCT of 6500K. The luminaire shall be compliant with IP20 and IK02 classification. Luminaire shall be designed to emit at least 1500 system lumens with maximum system wattage of 13.5 Watts. The lumanaire should have outstanding backlit solution efficacy.The luminaire shall be designed so as to ensure lumen depreciation of up to 30% over 50k burning hours @ design ambient temp 45 deg C. The electronic driver used shall have a power factor >0.95 and THD <10% and have operating voltage range from 130-320V. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Similar to DN296B LED15S-6500 PSU WH (Toilets) | NO | 48
D | Supply, installation, testing and commissioning of LED Linear 1x4 recessed fixture - 42 Watt, with a system lumen output of 3000 lumens at an efficacy of >65 lm/W (Similar to Philips Catalogue no. RC869 B W30 L120 LED or equivalent). The luminaire shall have powder coated CRCA housing and light output is by means of Semi High Gloss optics with 3D Lamellae and High Purity Anodized Aluminium mirrors. (Concourse & Platform Public Area) | NO | 834
E | Supply, installation, testing and commissioning of LED trunking system - 40 Watt , with a system lumen output of 4000 lumens and a minimum system efficacy of 100 lumen/watt (Similar to Philips Catalogue no. LL199X 1XDLED40-6500 PSE OD WH or equivalent). The luminaire shall have a extrusion housing and light emitted shall have a CRI>80 with rated system lifetime of 50,000 hours at L70. The extrusion housing shall be available in 4', 8' and 12' sections. (Platform Public Area) | NO | 104
F | Supply, installation, testing and commissioning of surface mounted LED Batten - 38 Watt (Similar to Philips Catalogue no. BN 108C LED 40S PSU CDL WH 919515810658 or equivalent), with a system lumen output of 4000 lumens and a minimum system efficacy of 100 lumen/watt. The luminaire shall have a CRI of greater than 80 with rated system lifetime of 50,000 hours at L70. The luminaire is made of CRCA housing and shall have diffused optics. (BOH without False Ceiling Area) | NO
F | Mirror Optic Recess mounted luminaries (Similar to Philips catalogue.No TCS 255 / 2x28 OR Keselec equivalent subject to approval by ER, Catalog no Pharma (Sym/Asym) 2x28 ) with housing made of white powder coated CRCA sheet steel, accommodating all electrical accessories pre-wired upto a terminal block. It should have high efficiency mirror optic anodised aluminium reflector for symmetrical and asymmetrical light distribution and must conform to Ingress Protection Classification of IP 54 (for dust and moisture protection). The luminaries should be suitable for 2 x 28W Tubular Flourescent Lamps and supplied with 2 Nos 28W Tubular Flourescent Lamps. | NO
H | Supply of Integral LED 4 ftwaterproof luminaire with UV Shielded polycarbonate housing and openable end caps. The luminaire should have a color consistency SDCM < 5, CRI > 80 and CCT of 6500K. The luminaire shall be compliant with IP65 and IK08 classification. Luminaire shall be designed to emit at least 4400 nominal lumens with maximum system wattage of 20 watts at a system efficacy of atleast 120 lumen/watt. The luminaire shall be designed so as to ensure lumen depreciation of up to 30% over 50k burning hours @ design ambient temp 45 deg C. Luminaire to be flickerfree with ripple <5%.The electronic driver used shall have a power factor >0.95 and THD <10% and suitable for an operationg voltage range of 140-270V ACThe electronic driver used shall have a power factor >0.95 and THD <10% and has high low cutoff with auto restart suitable for an operationg voltage range of 140-270V AC with high voltage cut off at 325. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters.Similar to WT201C LED44S-6500 PSU L120 S2(UNDERCROFT AREA) | NO | 106
I | Supply of LED Bulkhead with pressure die cast aluminium housing and PC diffuser. The fixture should have CRI > 80 and CCT of both 6500K. The luminaire shall be compliant with IP65 and IK08 classification. Luminaire shall be designed to emit at least 700 nominal lumens and maximum system wattage of 6.5 Watts. T.The luminaire shall be designed so as to ensure lumen depreciation of up to 30% over 25k burning hours @ design ambient temp 45 deg C. The electronic driver used shall have a power factor >0.9 and THD <20% . Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Similar to WT140W LED7S CW PSU S1 PC.(Shaft Area) | NO | 9
|  | NO | 9
J | Mirror Optic, recessed mounted Luminaries (Similar to Philips catalogue.No TBS/TCS 255 / 228 OR Keselec Catalog no.Pharma 2x28HF) with housing made of white powder coated CRCA Sheet Steel, accomodating all electrical accessories pre-wired upto a terminal box. It should have high efficiency mirror optic anodised aluminium reflector and must conform to Ingress Protection Classification of IP 54 (for dust and moisture Protection). The Luminaries should be suitable for 2 x 28W Tubular Flourescent lamp and supplied with 2 Nos. 28W Tubular Flourescent Lamp. | NO | 445
K | Supply of Mirror Optic, Surface mounted Luminaries (Similar to Philips catalogue No. TCS 399 / 228 OR Keselec Catalog no. Airolux DL 2/28W HF) or equivelent as per approved list, with housing made of powder coated CRCA Sheet Steel, accomodating all electrical accessories . It should have high efficiency mirror optic reflector . The Luminaries should be suitable for 2 x 36W Tubular Flourescent lamp and supplied with 2 Nos. 36W Tubular Flourescent Lamp. | NO | 360
L | Mirror Optic Recess mounted luminaries (Similar to Philips catalogue.No TBS 669 / 128 D6 OR Keselec Catalog no.CT lux DL 1x28HF) with housing made of white powder coated CRCA sheet steel, accommodating all electrical accessories pre-wired upto a terminal block. It should have high efficiency mirror optic reflector of high quality aluminium with parabolic side reflector, 3D cross lamallae with fresnell top and concave lower contour. The luminaries should be suitable for 1 x 28W Tubular Flourescent Lamps and supplied with 1 Nos 28W Tubular Flourescent Lamps. | NO | 10
N | Tunnel luminaire with high impact resistance IK10, IP-65 weather proof type, industrail LED type with housing and fire resistant low smoke halogen free type and non combustible materials (suitable for loop in & loop out with 4x4 sq mm/4x2.5 sq mm cable). similar to Phillips Cat BWP 120 LED 16 CWPC S1, as per specifications. | NO | 210
O | Bulk Head luminaries (Similar to Philips Catalogue No FXC 101 OR Keselec Catalog no. KBH 1x9 W) suitable for mounting on wall / ceiling having -Single piece pressure die cast Aluminium housing - Wire Guard made of powder coated MS - Heat resistant Glass cover The luminaries must conform to Ingress Protection Classification of IP 54 (for dust and Moisture Protection ). The luminaries should be suitable for 1 x 9W CFL lamp and supplied with 1 No. 9W CFL lamp and control accessories. | NO | 25
Q | Surface/Suspended type moisture proof diffuser luminiare with housing made of grey, high impact resistant polycarbonate, with Non-ageing gasket consisting of 2-component polyurethane foam. Difuser made of one piece injection moulded high impact resistant polycarbonate also computer optimised internal prismatic structure for precise direction of light and glare reduction, with difuser clips made of stainless steel, roll formed galvanised steel reflector that is enamelled white and can be suspended from either side of the housing. Suitable for 2x28W FTL Lamp prewired upto a terminal box with lamp. Having IP 65 (similar to Philips catalogue No. TCW 450 \ 2 x 28W HF or Keselec make sub 2x28W HF) and supplied with 2 Nos 28W Tubular Flourescent Lamps. | NO | 10
FL-1 | Compact, sturdy, general purpose floodlight luminaries (Similar to Philips catalogue. No TEMPO3 SWF 330 SK type OR Keselec make KSFL/250W/ SON-T) with integral gear, electrochemically brightened and anodized high purity aluminium reflector of symmetrical type. The luminaries must be adjustable with rugged, non corrosive pressure die cast aluminium housing and black powder coated finish and must be suitable for column mounting. It should have cover made of heat resistant toughened glass and the must be conforming to Ingress Protection Classification of IP 65 (for dust and moisture protection). The luminaries should be suitable for, and supplied with, One No 250W Sodium Vapour lamp. | NO | 20
FL-2 | Compact, sturdy, general purpose floodlight luminaries (Similar to Philips catalogue. No TEMPO3 MWF 330\250 AK HPI -T PLUS lamp OR Keselec make KSFL 250W/ HPI-T Plus) with integral gear, electrochemically brightened and anodized high purity aluminium reflector of symmetrical type. The luminaries must be adjustable with rugged, non corrosive pressure die cast aluminium housing and black powder coated finish and must be suitable for column mounting. It should have cover made of heat resistant toughened glass and the must be conforming to Ingress Protection Classification of IP 65 (for dust and moisture protection). The luminaries should be suitable for, and supplied with, One No 250W Metal halide lamp.(For double height area) | NO | 10
5.2 | Supply, Installation,Testing and Commission of Separate set of Nickel Cadmium battery with battery charger compatibles with all types of fixture mentioned above except Metal Halide & Flood Light type of fixtures with 2 hours back-up. | NO | 445