## outdoor yellow
TECHNICAL SPECIFICATIONS FOR LED OUTDOOR LIGHT LUMINARIES (YELLOW)
Sl. No. | DESCRIPTION |  |  | Firm's Confirmation
1 | GENERAL DESCRIPTION :
This Specifications covers design, manufacture, testing at manufacturer's Works, packing, supply, delivery of LED outdoor Light luminaries of Warm white.
2 | SCOPE :
A | Supply of Luminaries
| Description | Material Code | Qty
3 | Technical Specifications:
The LED Luminaires shall be as per the following parameters and no deviations are acceptable.
A | GENERAL:
a | The LED street light modules will confirm to IS 10322, and powered by latest bright LEDs (Phillips Lumileds/ Cree/ Osram/ Nichia/ LG/ Samsung makes only) with high efficiency and meeting LM-80 and LM-79 standards. Makes of light fittings : Phillips, Osram, GE Venture, Wipro, Crompton, Bajaj, Havells, Halonix,Jaquar, Eveready, Syska, Surya, Keselec, Poly Cab only. Only specified makes nentioned above are acceptable and other makes are not acceptable.
| Description | Outdoor (Warm White Type)
b | Luminarie Wattage | As per enquiry
c | LED luminary eficacy | > 100 Lumens/Watt
d | Life Span @ 70% light output | > 50000 Hrs.
e | Uniformity Ratio (E min / E avg) | 0.3
f | Control of Distribution | Fully Cutoff
g | Constant lux (The voltage variations / fluctuations in the specified voltage range shall not impinge upon the LUX levels it produces) | At 140V to 270V
h | Driver current (With Constant Current Driver) | <1500ma/ LED
i | Driver efficiency | > 90%
j | Beam angle of the luminaire
k | Color Temperature | 3000K
l | P/N Junction temperature (High thermal conduction must be achieved by use of silicon heat conductive greases as adhesive) | <85 ºC
m | Luminaire Body Temperature | The Body Temperature shall be < Ambient+40º C even after continuous burning of Luminaire for 24 Hrs
n | Colour Rendering Index (CRI) | > 70
B | ELECTRICAL
a | AC Input Voltage Range | 140V to 270V AC
b | Under voltage cut-off & over voltage Cut-off | To be Provided
c | AC Input frequency .( The LED circuitry shall function at an operating frequency that must be greater than 120 Hz to prevent perceptible flicker to the unaided eye over the entire voltage range specified above. ) | 50 Hz
d | Power Factor (Source Power Factor varies from 0.5 Lag to 0.5 Lead) | > 0.95
e | Luminary Wattage variance at 140 V to 270 V | + 10%
f | Luminary Lux Levels Variance at 140 V to 270 V | ± 5%
g | Total Harmonic Distortion(THD) | < 10%
h | Electrical Connection System | 3 wire system
i | System of earthing (The luminaries offered shall conform to Level-1 classification) | Solidly grounded
j | There shall be electrical isolation between input and output circuits of the driver. | To be complied
k | surge protection | on board ≥ 6kv and ≥10KV External with potted driver ( Inside Housing)
L | Driver | Potted Driver
C | MECHANICAL
a | Construction of Casing | High Pressure Die Cast Aluminum with integrated heat sink
b | Finish | PDC Powder Coated & colour
c | Heat Sink type (It shall be designed in such a way that the heat generated within the LED source is efficiently dissipated to the surrounding atmosphere without abnormal rise in temperature. Any debris build up shall not degrade heat dissipation performance of the luminaries.) | High Pressure Die Cast Aluminum with integrated heat sink
d | Lamp Cover | Toughened Glass
e | Secondary Optics/Lense for street lights & Flood Lights | Polycarbonate lens/silicon
f | IP Level | IP-66
g | Impact Resistance | IK07
h | Mounting | Surface / Suspended type. Street lights along with bolts & nuts. Flood lights shall have adjustable tilt design and the mounting bracket shall of suitable thickness and also with bolt & Nuts
i | Application of Illumination | For Open cast Mining
j | Firm's Offer/confirmation
| Gross Weight and Dimensions (L x W x T) of Luminaries (Efforts shall be made to keep the overall outer dimensions as minimum as possible with out compromising on the performance, mainly thermal management of the luminaire ) | Tobe furnished
4 | Technical Specifications of Luminaries ( Rating Wise)
a | LED Luminaries Wattage Rating (Luminary wise) | Tobe furnished
b | Firm's Offer/confirmation
| Light Source | High power Warm white LEDs
c | Firm's Offer/confirmation
| Minimum light output (Lumens) from luminare | Tobe furnished
5 | CONNECTING CABLE FOR OUTDOOR FITTINGS
a | Connecting cable, from electronic circuit (PCB) to Driver circuit which will be fixed in side of housing, is of copper, 3 core with colour indication, multi strand, PVC insulated, 1.1 KV grade and the current carrying capacity shall be 200% of its rated current.
b | Cable Outlet: Suitable circular hole shall be provided at the bottom of the fitting with fire resistance high grade engineering plastic glands securely fixed to the body on both sides by check nuts. The outgoing cable from fitting to power line shall be clamped to the inside base of the body to ensure fixing of the cable and suitable 'O' ring shall be provided at the cable entry to prevent dust / moisture entry and shall confirm to IP-66 protection. The cable shall be 3 core, aluminium cable with colour indication, multi strand, PVC insulated, 1.1 KV grade and the current carrying capacity shall be 200% of its rated current.
c | The earth core, having distinguished colour, shall be connected inside properly in view of solid earthing system.
6 | SAFETY PROTECTIONS:
Luminaries shall be designed and constructed in such a way as to avoid incursion of any danger while using them and shall ensure the following:
a | Personnel safety against electrical shock, effects of excessive temperature & spread of fire.
b | The material used in the construction of driver printed boards, driver enclosure etc. shall be non-flammable and heat resistant.
7 | STANDARDS
The materials shall conform in all respects to the following relevant Standard Specifications with latest amendments thereto.
a | IS:10322 or latest
b | Transient voltages, Voltage dips and flactuations shall conform to IEC:61000-4-5 or latest
8 | TEST REPORTS / TEST CERTIFICATES:
A | Type Tests :
The luminaries shall be fully type tested at an NABL by the bidder as per IS:10322. Copy of latest type test reports shall be furnished along with the Bid. The Bids received without type test reports by NABL will not be considered. (Enclose SCOPE of testing of Accrediation certificate).
a | Visual examination
b | Resistance to dust and moisture
c | Insulation resistance and electric strength
d | Photometry test
B | Acceptance Tests
These tests shall be carried out, as stipulated in BIS/IEC standards, by an inspecting authority at the suppliers premises on sample taken from a lot for the purpose of acceptance of a lot. Acceptance tests shall not be carried out from particular size from the lot on which type tests have already been conducted.
a | Visual examination
b | Resistance to dust and moisture
c | Insulation resistance and electric strength
d | Photometry test
9 | Documents to be submitted along with the offer :
a | The bidder shall furnish G A dimensional drawings with all views of Luminaire pertaining to all the models offered along with the technical bid .
b | Type test certificates as mentioned under Sl.No.8A of technical specifications
c | Technical Catalogue of product
d | Lumen Depreciation Curve of LEDs used (supplied by LED manufacturer)
e | Polar Diagram of Luminaire tested in certified laboratory
f | LM79 Measurement Report for the luminaire from NABL Accredited Laboratory
g | LM 80 report for the LEDs used (Supplied by the LED manufacturer ) . Enclose LED purchase Invoice.
h | L70 report for claimed life of LEDs in hours (Supplied by the LED manufacturer )
i | Performance reports along with order copies of LED luminaire supplies made to public sector companies and Government organisations shall be enclosed. Private sector performance reports will not be considered.
j | Only manufacturers shall submit the tenders either directly or through their authorized Distributors/Authorized Dealers. Original letters of authorization and Valid Certificates of Authorized Distributorship/Dealership must be enclosed along with the technical bid of the offers in case tenders are submitted through Authorized Distributors/Dealers. Other wise the tenders will be summarily rejected.
10 | DOCUMENTS TO BE SUBMITTED ALONG WITH EACH CONSIGNMENT.
a | The Firm shall submit rating wise 3 sets of approved G A dimensional drawings with name plate and all views of Luminaire along with each consignment.
b | 3 sets of operating manuals / technical leaflets rating wise giving all the details of Installation, operation and maintenance shall be supplied along with each consignment.
11 | MARKING
The following information shall be distinctly and indelibly marked / embossed / engraved on each luminaire housing for using reference during performance study and warranty replacements.
a | Year of manufacture, batch Number and Serial number
b | Name of manufacturer
c | Rated Wattage and Voltage
12 | GUARANTEE TERMS AND CONDITIONS
a | The Luminaries should be guaranteed for satisfactory operation for a period of 5 years from the date of supply of Luminaries. Failures shall include failure / deterioration of LEDs in terms of performance like guaranteed luminous efficiency, high junction temperature, and abnormal lamp lumen depreciation, deterioration of lens, driver unit and quality of light. In the event of single LED source getting defective, the entire array / module shall be repaired/ replaced by the supllier at free of cost .The transportation of defective Luminaries shall be under firms scope.

## outdoor white
TECHNICAL SPECIFICATIONS FOR LED OUTDOOR LIGHT LUMINARIES
Sl. No. | DESCRIPTION |  |  | Firm's Confirmation
1 | GENERAL DESCRIPTION :
This Specifications covers design, manufacture, testing at manufacturer's Works, packing, supply, delivery of LED outdoor Light luminaries of Cool white.
2 | SCOPE :
A | Supply of Luminaries
| Description | Material Code | Qty
| LED STREET LIGHT FITTING 100W 230V | 1472552453 | 100
| LED STREET LIGHT FITING 150W 230V | 1472552416 | 25
| LED FLOOD/BEAM LIGHT FITTING 200W 230V | 1472552490 | 20
| LED STREET LIGHT FITTING 30W 230V | 1472552337 | 200
| LED TUBE LIGHT FITTING 20W 230V | 1472552430 | 300
3 | Technical Specifications:
The LED Luminaires shall be as per the following parameters and no deviations are acceptable.
A | GENERAL:
a | The LED street light modules will confirm to IS 10322, and powered by latest bright LEDs (Phillips Lumileds/ Cree/ Osram/ Nichia/ LG/ Samsung makes only) with high efficiency and meeting LM-80 and LM-79 standards. Makes of light fittings : Phillips, Osram, GE Venture, Wipro, Crompton, Bajaj, Havells, Halonix,Jaquar, Eveready, Syska, Surya, Keselec, Poly Cab only. Only specified makes nentioned above are acceptable and other makes are not acceptable.
| Description | Outdoor (Cool White Type)
b | Luminarie Wattage | As per enquiry
c | LED luminary eficacy | > 100 Lumens/Watt
d | Life Span @ 70% light output | > 50000 Hrs.
e | Uniformity Ratio (E min / E avg) | 0.3
f | Control of Distribution | Fully Cutoff
g | Constant lux (The voltage variations / fluctuations in the specified voltage range shall not impinge upon the LUX levels it produces) | At 140V to 270V
h | Driver current (With Constant Current Driver) | <1500ma/ LED
i | Driver efficiency | > 90%
j | Beam angle of the luminaire | 120º
k | Color Temperature | 5700K to 6500K
l | P/N Junction temperature (High thermal conduction must be achieved by use of silicon heat conductive greases as adhesive) | <85 ºC
m | Luminaire Body Temperature | The Body Temperature shall be < Ambient+40º C even after continuous burning of Luminaire for 24 Hrs
n | Colour Rendering Index (CRI) | > 70
B | ELECTRICAL
a | AC Input Voltage Range | 140V to 270V AC
b | Under voltage cut-off & over voltage Cut-off | To be provided
c | AC Input frequency .( The LED circuitry shall function at an operating frequency that must be greater than 120 Hz to prevent perceptible flicker to the unaided eye over the entire voltage range specified above. ) | 50 Hz
d | Power Factor (Source Power Factor varies from 0.5 Lag to 0.5 Lead) | > 0.95
e | Luminary Wattage variance at 140 V to 270 V | + 10%
f | Luminary Lux Levels Variance at 140 V to 270 V | ± 5%
g | Total Harmonic Distortion(THD) | < 10%
h | Electrical Connection System | 3 wire system
i | System of earthing (The luminaries offered shall conform to Level-1 classification) | Solidly grounded
j | There shall be electrical isolation between input and output circuits of the driver. | To be complied
k | surge protection | on board ≥ 6kv and ≥10KV External with potted driver ( Inside Housing)
L | Driver | Potted Driver
C | MECHANICAL
a | Construction of Casing | High Pressure Die Cast Aluminum with integrated heat sink
b | Finish | PDC Powder Coated & colour
c | Heat Sink type (It shall be designed in such a way that the heat generated within the LED source is efficiently dissipated to the surrounding atmosphere without abnormal rise in temperature. Any debris build up shall not degrade heat dissipation performance of the luminaries.) | High Pressure Die Cast Aluminum with integrated heat sink
d | Lamp Cover | Toughened Glass
e | Secondary Optics/Lense for street lights & Flood Lights | Polycarbonate lens/silicon
f | IP Level | IP-66
g | Impact Resistance | IK07
h | Mounting | Surface / Suspended type. Street lights along with bolts & nuts. Flood lights shall have adjustable tilt design and the mounting bracket shall of suitable thickness and also with bolt & Nuts
i | Application of Illumination | For Yard, Stadiums, Parks, Junction lighting.etc
j | Firm's Offer/confirmation
| Gross Weight and Dimensions (L x W x T) of Luminaries (Efforts shall be made to keep the overall outer dimensions as minimum as possible with out compromising on the performance, mainly thermal management of the luminaire ) | Tobe furnished
4 | Technical Specifications of Luminaries ( Rating Wise)
a | LED Luminaries Wattage Rating (Luminary wise) | Tobe furnished
b | Firm's Offer/confirmation
| Light Source | High power Cool white LEDs
c | Firm's Offer/confirmation
| Minimum light output (Lumens) from luminare | Tobe furnished
5 | CONNECTING CABLE FOR OUTDOOR FITTINGS
a | Connecting cable, from electronic circuit (PCB) to Driver circuit which will be fixed in side of housing, is of copper, 3 core with colour indication, multi strand, PVC insulated, 1.1 KV grade and the current carrying capacity shall be 200% of its rated current.
b | Cable Outlet: Suitable circular hole shall be provided at the bottom of the fitting with fire resistance high grade engineering plastic glands securely fixed to the body on both sides by check nuts. The outgoing cable from fitting to power line shall be clamped to the inside base of the body to ensure fixing of the cable and suitable 'O' ring shall be provided at the cable entry to prevent dust / moisture entry and shall confirm to IP-66 protection. The cable shall be 3 core, aluminium cable with colour indication, multi strand, PVC insulated, 1.1 KV grade and the current carrying capacity shall be 200% of its rated current.
c | The earth core, having distinguished colour, shall be connected inside properly in view of solid earthing system.
6 | SAFETY PROTECTIONS:
Luminaries shall be designed and constructed in such a way as to avoid incursion of any danger while using them and shall ensure the following:
a | Personnel safety against electrical shock, effects of excessive temperature & spread of fire.
b | The material used in the construction of driver printed boards, driver enclosure etc. shall be non-flammable and heat resistant.
7 | STANDARDS
The materials shall conform in all respects to the following relevant Standard Specifications with latest amendments thereto.
a | IS:10322 or latest
b | Transient voltages, Voltage dips and flactuations shall conform to IEC:61000-4-5 or latest
8 | TEST REPORTS / TEST CERTIFICATES:
A | Type Tests :
The luminaries shall be fully type tested at an NABL by the bidder as per IS:10322. Copy of latest type test reports shall be furnished along with the Bid. The Bids received without type test reports by NABL will not be considered. (Enclose SCOPE of testing of Accrediation certificate).
a | Visual examination
b | Resistance to dust and moisture
c | Insulation resistance and electric strength
d | Photometry test
B | Acceptance Tests
These tests shall be carried out, as stipulated in BIS/IEC standards, by an inspecting authority at the suppliers premises on sample taken from a lot for the purpose of acceptance of a lot. Acceptance tests shall not be carried out from particular size from the lot on which type tests have already been conducted.
a | Visual examination
b | Resistance to dust and moisture
c | Insulation resistance and electric strength
d | Photometry test
9 | Documents to be submitted along with the offer :
a | The bidder shall furnish G A dimensional drawings with all views of Luminaire pertaining to all the models offered along with the technical bid .
b | Type test certificates as mentioned under Sl.No.8A of technical specifications
c | Technical Catalogue of product
d | Lumen Depreciation Curve of LEDs used (supplied by LED manufacturer)
e | Polar Diagram of Luminaire tested in certified laboratory
f | LM79 Measurement Report for the luminaire from NABL Accredited Laboratory
g | LM 80 report for the LEDs used (Supplied by the LED manufacturer ) . Enclose LED purchase Invoice.
h | L70 report for claimed life of LEDs in hours (Supplied by the LED manufacturer )
i | Performance reports along with order copies of LED luminaire supplies made to public sector companies and Government organisations shall be enclosed. Private sector performance reports will not be considered.
j | Only manufacturers shall submit the tenders either directly or through their authorized Distributors/Authorized Dealers. Original letters of authorization and Valid Certificates of Authorized Distributorship/Dealership must be enclosed along with the technical bid of the offers in case tenders are submitted through Authorized Distributors/Dealers. Other wise the tenders will be summarily rejected.
10 | DOCUMENTS TO BE SUBMITTED ALONG WITH EACH CONSIGNMENT.
a | The Firm shall submit rating wise 3 sets of approved G A dimensional drawings with name plate and all views of Luminaire along with each consignment.
b | 3 sets of operating manuals / technical leaflets rating wise giving all the details of Installation, operation and maintenance shall be supplied along with each consignment.
11 | MARKING
The following information shall be distinctly and indelibly marked / embossed / engraved on each luminaire housing for using reference during performance study and warranty replacements.
a | Year of manufacture, batch Number and Serial number
b | Name of manufacturer
c | Rated Wattage and Voltage
12 | GUARANTEE TERMS AND CONDITIONS
a | The Luminaries should be guaranteed for satisfactory operation for a period of 5 years from the date of supply of Luminaries. Failures shall include failure / deterioration of LEDs in terms of performance like guaranteed luminous efficiency, high junction temperature, and abnormal lamp lumen depreciation, deterioration of lens, driver unit and quality of light. In the event of single LED source getting defective, the entire array / module shall be repaired/ replaced by the supllier at free of cost .The transportation of defective Luminaries shall be under firms scope.

## Indoor
TECHNICAL SPECIFICATIONS FOR LED INDOOR LIGHT LUMINARIES
Sl. No. | DESCRIPTION |  |  | Firm's Confirmation
1 | GENERAL DESCRIPTION :
This Specifications covers design, manufacture, testing at manufacturer's Works, packing, supply, delivery of LED indoor Light luminaries of Cool white.
2 | SCOPE :
A | Supply of Luminaries
| Description | Material Code | Qty
3 | Technical Specifications:
The LED Luminaires shall be as per the following parameters and no deviations are acceptable.
A | GENERAL:
a | The LED street light modules will confirm to IS 10322, and powered by latest bright LEDs (Phillips Lumileds/ Cree/ Osram/ Nichia/ LG/ Samsung makes only) with high efficiency and meeting LM-80 and LM-79 standards. Makes of light fittings : Phillips, Osram, GE Venture, Wipro, Crompton, Bajaj, Havells, Halonix,Jaquar, Eveready, Syska, Surya, Keselec, Poly Cab only. Only specified makes nentioned above are acceptable and other makes are not acceptable.
| Description | Indoor
b | Luminarie Wattage | As per enquiry
c | LED luminary eficacy | > 100 Lumens/Watt
d | Life Span @ 70% light output | > 50000 Hrs.
e | Uniformity Ratio (E min / E avg) | 0.3
f | Control of Distribution | Fully Cutoff
g | Constant lux (The voltage variations / fluctuations in the specified voltage range shall not impinge upon the LUX levels it produces) | At 140V to 270V
h | Driver current (With Constant Current Driver) | < 500 ma / LED
i | Driver efficiency | > 85%
j | Beam angle of the luminaire | 120º
k | Color Temperature | 5700K to 6500K
l | P/N Junction temperature (High thermal conduction must be achieved by use of silicon heat conductive greases as adhesive) | <85 ºC
m | Luminaire Body Temperature | The Body Temperature shall be < Ambient+35º C even after continuous burning of Luminaire for 24 Hrs
n | Colour Rendering Index (CRI) | >70
B | ELECTRICAL
a | AC Input Voltage Range | 140V to 270V AC
b | Under voltage cut-off & over voltage Cut-off | **
c | AC Input frequency .( The LED circuitry shall function at an operating frequency that must be greater than 120 Hz to prevent perceptible flicker to the unaided eye over the entire voltage range specified above. ) | 50 Hz
d | Power Factor (Source Power Factor varies from 0.5 Lag to 0.5 Lead) | > 0.95
e | Luminary Wattage variance at 140 V to 270 V | + 10%
f | Luminary Lux Levels Variance at 140 V to 270 V | ± 5%
g | Total Harmonic Distortion(THD) | < 15%
h | Electrical Connection System | 2 wire system
i | System of earthing (The luminaries offered shall conform to Level-1 classification) | **
j | There shall be electrical isolation between input and output circuits of the driver. | To be complied
k | surge protection | upto to 3.0KV
L | Driver | ***
C | MECHANICAL
a | Construction of Casing | Extruded Aluminium/ CRCA
b | Finish | Anodised/ Powder coated
c | Heat Sink type (It shall be designed in such a way that the heat generated within the LED source is efficiently dissipated to the surrounding atmosphere without abnormal rise in temperature. Any debris build up shall not degrade heat dissipation performance of the luminaries.) | Aluminium Metal Core PCB
d | Lamp Cover | UV stabilized polycorbonate Glass/ Teflon glass
e | Secondary Optics/Lense for street lights & Flood Lights | NA
f | IP Level | IP-20
g | Impact Resistance | **
h | Mounting | 4 feet tube light--wall mounted., Ceiling Lights: 2 Feet X 2 Feet recessed mounting
i | Application of Illumination | Office Rooms
j | Firm's Offer/confirmation
| Gross Weight and Dimensions (L x W x T) of Luminaries (Efforts shall be made to keep the overall outer dimensions as minimum as possible with out compromising on the performance, mainly thermal management of the luminaire ) | Tobe furnished
4 | Technical Specifications of Luminaries ( Rating Wise)
a | LED Luminaries Wattage Rating (Luminary wise) | Tobe furnished
b | Firm's Offer/confirmation
| Light Source | Cool White
c | Firm's Offer/confirmation
| Minimum light output (Lumens) from luminare | Tobe furnished
5 | CONNECTING CABLE FOR OUTDOOR FITTINGS
a | Connecting cable, from electronic circuit (PCB) to Driver circuit which will be fixed in side of housing, is of copper, 3 core with colour indication, multi strand, PVC insulated, 1.1 KV grade and the current carrying capacity shall be 200% of its rated current.
b | Cable Outlet: Suitable circular hole shall be provided at the bottom of the fitting with fire resistance high grade engineering plastic glands securely fixed to the body on both sides by check nuts. The outgoing cable from fitting to power line shall be clamped to the inside base of the body to ensure fixing of the cable and suitable 'O' ring shall be provided at the cable entry to prevent dust / moisture entry and shall confirm to IP-66 protection. The cable shall be 3 core, aluminium cable with colour indication, multi strand, PVC insulated, 1.1 KV grade and the current carrying capacity shall be 200% of its rated current.
c | The earth core, having distinguished colour, shall be connected inside properly in view of solid earthing system.
6 | SAFETY PROTECTIONS:
Luminaries shall be designed and constructed in such a way as to avoid incursion of any danger while using them and shall ensure the following:
a | Personnel safety against electrical shock, effects of excessive temperature & spread of fire.
b | The material used in the construction of driver printed boards, driver enclosure etc. shall be non-flammable and heat resistant.
7 | STANDARDS
The materials shall conform in all respects to the following relevant Standard Specifications with latest amendments thereto.
a | IS:10322 or latest
b | Transient voltages, Voltage dips and flactuations shall conform to IEC:61000-4-5 or latest
8 | TEST REPORTS / TEST CERTIFICATES:
A | Type Tests :
The luminaries shall be fully type tested at an NABL by the bidder as per IS:10322. Copy of latest type test reports shall be furnished along with the Bid. The Bids received without type test reports by NABL will not be considered. (Enclose SCOPE of testing of Accrediation certificate).
a | Visual examination
b | Resistance to dust and moisture
c | Insulation resistance and electric strength
d | Photometry test
B | Acceptance Tests
These tests shall be carried out, as stipulated in BIS/IEC standards, by an inspecting authority at the suppliers premises on sample taken from a lot for the purpose of acceptance of a lot. Acceptance tests shall not be carried out from particular size from the lot on which type tests have already been conducted.
a | Visual examination
b | Resistance to dust and moisture
c | Insulation resistance and electric strength
d | Photometry test
9 | Documents to be submitted along with the offer :
a | The bidder shall furnish G A dimensional drawings with all views of Luminaire pertaining to all the models offered along with the technical bid .
b | Type test certificates as mentioned under Sl.No.8A of technical specifications
c | Technical Catalogue of product
d | Lumen Depreciation Curve of LEDs used (supplied by LED manufacturer)
e | Polar Diagram of Luminaire tested in certified laboratory
f | LM79 Measurement Report for the luminaire from NABL Accredited Laboratory
g | LM 80 report for the LEDs used (Supplied by the LED manufacturer ) . Enclose LED purchase Invoice.
h | L70 report for claimed life of LEDs in hours (Supplied by the LED manufacturer )
i | Performance reports along with order copies of LED luminaire supplies made to public sector companies and Government organisations shall be enclosed. Private sector performance reports will not be considered.
j | Only manufacturers shall submit the tenders either directly or through their authorized Distributors/Authorized Dealers. Original letters of authorization and Valid Certificates of Authorized Distributorship/Dealership must be enclosed along with the technical bid of the offers in case tenders are submitted through Authorized Distributors/Dealers. Other wise the tenders will be summarily rejected.
10 | DOCUMENTS TO BE SUBMITTED ALONG WITH EACH CONSIGNMENT.
a | The Firm shall submit rating wise 3 sets of approved G A dimensional drawings with name plate and all views of Luminaire along with each consignment.
b | 3 sets of operating manuals / technical leaflets rating wise giving all the details of Installation, operation and maintenance shall be supplied along with each consignment.
11 | MARKING
The following information shall be distinctly and indelibly marked / embossed / engraved on each luminaire housing for using reference during performance study and warranty replacements.
a | Year of manufacture, batch Number and Serial number
b | Name of manufacturer
c | Rated Wattage and Voltage
12 | GUARANTEE TERMS AND CONDITIONS
a | The Luminaries should be guaranteed for satisfactory operation for a period of 5 years from the date of supply of Luminaries. Failures shall include failure / deterioration of LEDs in terms of performance like guaranteed luminous efficiency, high junction temperature, and abnormal lamp lumen depreciation, deterioration of lens, driver unit and quality of light. In the event of single LED source getting defective, the entire array / module shall be repaired/ replaced by the supllier at free of cost .The transportation of defective Luminaries shall be under firms scope.