## 2100011711
ITEM NUMBER | MATERIAL CODE | DESCRIPTION | QUANTITY | UOM | TS PARAMETER | TS RANGE / VALUE | RESPONSE
1 | 2125449 | LUMINAIRE,IND,120W-140W | 800 | EA
LUMINAIRE,INDUSTRIAL
[5 empty] | TYPE | STREET LIGHT FITTING
[5 empty] | INGRESS PROTECTION | IP66
TYPE,LAMP
: LED(SMD/COB)
[5 empty] | MATERIAL,BODY | DIE-CAST ALUMINIUM
[5 empty] | RATING,POWER | 120W-140W
[5 empty] | 1) Ambient temperature range in deg C | 0-45 deg.
[5 empty] | 2)Input power | 230V Â±6%, 50Hz Â±3%.
[5 empty] | 3)Input Voltage Range | 150-270V.
4)AC Power Factor
>0.95
|  | RRRR |  |  | 5)System power consumption (w) - Input power for fixtures | 140W LED
Street light(MAX)
[5 empty] | 6)Spacing between street light poles | 3 0mtrs
[5 empty] | 7)Height of street light poles above road level | 10mtrs
[5 empty] | 8) Arm length of pole | 2.5mtrs
[5 empty] | 9)Width of road | 9mtrs
[5 empty] | 10)Mounting arra ngement | Suitable to mount on street light pole arm of
60 mm diameter at 15 deg angle.
[5 empty] | 11)Maintenance factor to be considered | 0.8
1 2) Average illumination level to be maintained on roads with UO
[5 empty] | >40% | 20 lux
13) Enclosure
i)Pressure Die cast Aluminium LMO6.
ii)Pu based powder coating to withstand highly corrosive,dusty & humid
atmosphere.
iii) Enclosure will have separate Driver box which is
integrated with
Enclosure. Access of driver box shall be with separate cover.
[5 empty] | 14)Degree of protection | IP 66(min) for the complete
fixture.
[5 empty] | 15)Glass type at bottom | Toughened Glass with impact protection rating
IK > 07.
16)Lumen efficacy of the complete Light Fi tting(System
[5 empty] | Efficacy) | Minimum 100 lumen per watt at minimum operating current and
controlled junction temperature of 85 deg C.
[5 empty] | 17)L umen efficacy of LED lamp | Minimum 150 lumen per watt at minimum
operating current and controlled junction temperature of 85 deg C.
[5 empty] | 18) LED Make & country of Manufacture | NICHIA(japan)/ CREE/
OSRAM/PHILIPS/CITIZEN(JAPAN).
[5 empty] | 19)Colour Rending Index(CRI) | >70
[5 empty] | 20)Colou r Temperature deg K | 5700Â±300K.
[5 empty] | 21)Junction Tempreature | Maximum upto 135 deg C.
[5 empty] | 22)Heat Sink | Housing acts as heat sink.
[5 empty] | 23)THD | <10 %
[5 empty] | 24)LED life as per LM80 criteria(minimum in burning hours) | 50000(min)
25)Maximum Lumen depreciation at 50,000 hours @25 Deg ambie nt
[5 empty] | Temperature along with deprecation | 30%
26)Driver Protections
a)Input over Voltage cut off at 300V AC to 350V AC. Auto recovery a t
320V AC.
b)Output over Voltage, short circuit protection
c)440V protection for > 1 hour.
[5 empty] | 27)Type of Driver | Constant Current/Const ant Voltage.
[5 empty] | 28)Efficiency of driver in percentage | >85%
[5 empty] | 29)Surge protection | Inbuilt Surge protection of 4KV with External
Surge P rotection of 10KV.
[5 empty] | 30)Driver Make | Inventronics/Meanwell/Fulham/Philips
[5 empty] | 31) Driver Construction | APFC.
[5 empty] | 32)PHOTOMETER LAB | Luminaire
manufacturer must have Photometer Lab in
INDIA.
[5 empty] | 33)Spares Support | Confirm spares support in INDIA for next ten years
from the date of supply.
[5 empty] | 34)SDCM(ANSI) | C78.377.
[5 empty] | 35)TEST CERTIFICATES | TEST CERTIFICATES TO BE SUBMITTED FOR THE MODEL &
LOT SUPPLIED BY THE SUPP LIER.
[5 empty] | i)LM 79 CERTIFICATE | From NABL accredited laboratory for the lighting
fixture.
[5 empty] | ii)LM 80 CERTIFICATE | From the LED chip manufac turer.
iii)Photo biological safety as per EN 62471 along with LM80 certificate.
[5 empty] | iv)EMI/EMC compliance | The offered LED drivers shoul d be EMI/EMC
compliant to relevant IS & OEC standards and documentary proofs to be
submitted for the same
v)Driver shall also comply the performance requirements as per
[5 empty] | IEC | 62384/IS: 16104.
[5 empty] | 36)Guarantee | Complete LED light fittings shall be guaranteed for at
least 5 years of operation, light output/light colour/colour quality
37)Reference list of offered light fitting in the last one year from
date of NIT submitted.
[5 empty] | 38)SPECIAL INSTRUCTION | EVERY SUPPLIED LAMP AND DRIVER SHOULD HAVE
UNIQUE IDENTIFICATION NUMBER.
39)SAMPLE R EQUIRED
i) Successful tenderer needs to supply three samples to the
indentor before bulk supply.
ii)Spare Drivers (same as the driv er in the light fitting supplied) are
to be supplied along with the complete light fittings. Quantity of
these spare drivers require d is 20% of the total supplied quantity of
complete Light fittings. Cost of the spare drivers is to be included in
the quoted price
of light fittings.
Gurantee
[5 empty] | Sample Required | Yes
[5 empty] | Test Certificate Required | Yes
************************************
For Office use Only
************************************
TA/TNA
Reasons for TNA
Remarks, if any
RFx Number | 2100011711
Bidder Code
Bidder Name