## Light fixture
CONSTRUCTION OF SUPER SPECIALTY HOSPITAL BLOCK UNDER PMSSY AT GOVERNMENT MEDICAL COLLEGE CAMPUS, SURAT DIST: SURAT
S.No. | Item No. | Item Description | Qty | Unit
552 | 552 | SECTION 5.00 LIGHT FIXTURE AND FAN ALL LIGHT FIXTURES SHALL COMPLY TECHNICAL PARAMETERS AS MENTIONED BELOW: 1.The Fixture and driver should be of same make only. 2.The manufacture should provided Complete TTC and quality assurance Plan for Fixtures during supply. 3.The Warranty letter for 5years should be provided by the Manufacturer. 4.Fixture should be warrantied for 5yrs for 50,000 hrs at L70 ( LM79 from NABL accredited Lab to be submitted along with Letter from Manufacturer for the Life class claim of L70 at 50,000 hrs.) 5.The product should be Manufactured in India (all the Components should be manufactured in India except the Led source which can be imported . (Approved Led source Nichia , Cree, Lumileds , Osram Only the Invoice copy of the Purchase of Led modules from these manufacturer"s need to be submitted).) 6. PF >=0.9 and THD <=15 Percentage ( Certificate need to be submitted from NABL Accredited lab) 7. The manufacturer should be ISO 9001 -2008 and ISO 14001 -2004 Company 8. The manufacturer should have its own NABL accredited Laboratory. Supply, Installation, testing and erecting of reccess/surface mounted 2ftX2ft 30Wluminaire with high performance LEDs, suitable for mounting with Armstrong / Grid ceiling.CRCA powder coated white after phosphochromate treatment.High efficiency long life LED package in integral module with system lumen efficacy of >110 lm/W and viewing angle of 120 degree to ensure better uniformity.Powered by an independent Isolated, SELV Output electronic LED driver (SMPS based constant current supply) with Output Short-circuit protection, Surge protection and other reliability test. Lumen Output of 3100 lumens.CRI >80, Color temperature 5700K, THD <10 Percentage and PF >0.95,IP20,IK03.Life class of 50,000 hrs at L70, Operating Temperature:-10 TO +45 DEG.C; Input Supply Voltage Range:140-270 V, Frequency :50-60 HZ; Internal Surge Protection:3 KV; Protection : Reverse Polarity, Open and Short Circuit. DRIVER SAFETY REQUIREMENT STANDARDS :IS 15885-2-13, TEST REPORT TO BE SUBMITTED; PHOTO BIOLOGICAL SAFETY NORMS: IS 16108, TEST CERTIFICATE TO BE SUBMITTED; CERTIFICATION: LM 79 FOR LUMINAIRE LM 80 FOR LED SOURCE. | 525 | Nos
553 | 553 | Supply, Installation, testing and erecting of reccess mounted 2ftX2ft 30 -40W.clean room Fixture made of MS powder coated white after phosphochromate treatment and High quality polycarbonate opal diffuser.High efficiency long life LEDs with lumen efficacy of >90 lm/W with system lumen 3400. Powered by an integral, Isolated, SELV Output electronic LED driver (SMPS based constant current supply) with Output Short-circuit protection, Surge protection. CCT 5700, CRI>80, THD<10 Percentage , PF>.95, Lumen Package>3200Lm(Fixture Efficacy), IP65, IK05.Life class of 50,000 hrs at L70, Operating Temperature:-10 TO +45 DEG.C; Input Supply Voltage Range:140-270 V, Frequency :50-60 HZ. DRIVER SAFETY REQUIREMENT STANDARDS :IS 15885-2-13, DRIVER PERFORMANCE REQUIREMENTS: IS 16104, PHOTO BIOLOGICAL SAFETY NORMS: IS 16108, CERTIFICATION: LM 79 FOR LUMINAIRE LM 80 FOR LED SOURCE. | 625 | Nos
554 | 554 | Supply, Installation, testing and erecting of suspended 24 WATT LED with minimum 2400 lumens 4 ft length luminaire made of Aluminum extruded housing in white powder coated finish and snap fit plastic moulded end caps, High transmittance PMMA opal profiled diffuser, control gear accessible and serviceable from bottom, suitable for standalone and continuous row mounting for endless line of light, High efficiency long life LED package in integral module with lumen efficacy > 95 Lm/W and viewing angle of 120 degree to ensure better uniformity.Powered by an integral isolated low THD electronic LED driver ( SMPS based constant current supply) with output short circuit protection, surge protection. Fixture Efficacy> 100Lm/W, CRI >80, Color temperature 5700K, THD <10 Percentage and PF >0.90,IP20,IK03.Life class of 50,000 hrs at L70, Operating Temperature:-10 TO +45 DEG.C; Input Supply Voltage Range:140-270 V, Frequency :50-60 HZ; Internal Surge Protection:3.5 KV; Protection : Reverse Polarity, Open and Short Circuit. DRIVER SAFETY REQUIREMENT STANDARDS :IS 15885-2-13, TEST REPORT TO BE SUBMITTED; PHOTO BIOLOGICAL SAFETY NORMS: IS 16108, TEST CERTIFICATE TO BE SUBMITTED; CERTIFICATION: LM 79 FOR LUMINAIRE LM 80 FOR LED SOURCE. | 1500 | Nos
555 | 555 | Supply, Installation, testing and erecting of reccess / surface mounted 18 W (150-200mm Dia.)with high performance LEDs.White powder coated, elegantly designed pressure die-cast aluminium heat sink for efficient dissipation and white finish polycarbonate ring for holding the diffuser. High quality polycarbonate opal concave diffuser.High efficiency long life SMD LED mounted on MCPCB with high system efficacy of 100 lm/W . Electronic driver Powered by integral SMPS based constant current electronic driver with lower THD, Output Short Circuit Protection, Surge Voltage Protection . Lumen Output of 1800 lumens, with Efifcacy>100Lm/W, CRI >80, Color temperature 5700K, THD <10 Percentage and PF >0.95,IP20,IK03.Life class of 50,000 hrs at L70, Operating Temperature:-10 TO +45 DEG.C; Input Supply Voltage Range:140-270 V, Frequency :50-60 HZ; Internal Surge Protection:3 KV; Protection : Reverse Polarity, Open and Short Circuit. DRIVER SAFETY REQUIREMENT STANDARDS :IS 15885-2-13, TEST REPORT TO BE SUBMITTED; PHOTO BIOLOGICAL SAFETY NORMS: IS 16108, TEST CERTIFICATE TO BE SUBMITTED; CERTIFICATION: LM 79 FOR LUMINAIRE LM 80 FOR LED SOURCE. | 2500 | Nos
556 | 556 | Supply, Installation, testing and erecting of reccess / surface mounted 30W (150-200mm Dia.) downlight made of powder coated, elegantly designed pressure die-cast aluminium housing / heat sink for efficient heat dissipation and white finish PDC ring for holding the diffuser.High purity faceted PC metalized glossy reflector.High quality PMMA diffuser in clear finish for uniform light distribution.High efficiency long life COB LED mounted on MCPCB.System efficacy of 100 lm/W.Powered by an independent, isolated, SELV output electronic LED driver (SMPS based constant current supply) with Output Short-circuit protection, Surge Voltage protection. Lumen Output of 3000 lumens.Beam Angle 40 degree ,CRI >80, Lumen Package >2900Lm, Color temperature 5700K, THD<10 Percentage and PF >0.95,IP20,IK03.Life class of 50,000 hrs at L70, Operating Temperature:-10 TO +45 DEG.C; Input Supply Voltage Range:140-270 V, Frequency :50-60 HZ; Internal Surge Protection:3 KV; Protection : Reverse Polarity, Open and Short Circuit. DRIVER SAFETY REQUIREMENT STANDARDS :IS 15885-2-13, TEST REPORT TO BE SUBMITTED; PHOTO BIOLOGICAL SAFETY NORMS: IS 16108, TEST CERTIFICATE TO BE SUBMITTED; CERTIFICATION: LM 79 FOR LUMINAIRE LM 80 FOR LED SOURCE. | 1700 | Nos
557 | 557 | Supply, Installation, testing and erecting of energy saving Energy Efficient (1 - 2 ft) 9-12W, ultra slim co-extruded polycarbonate channel with housing part in white finish and diffuser part in reeded opal finish.White finish ABS end caps with decorative circular coloured polycarbonate cap snap fitted on the end cap to enhance the aesthetic of the fixture. These end caps are snap-fitted to the fixture.High efficiency long life LED with viewing angle of 120º.Powered by an integral isolated low THD electronic LED driver ( SMPS based constant current supply) with output short circuit protection, surge protection.Can be fixed directly into the wall/ ceiling by means of mounting SS clips provided with the fixture. Lumen Output of 950 lumens with System efficacy of > 105lm/W .CRI >80, Color temperature 5700K, THD <20 Percentage and PF>0.95,IP20 . Life class of 35,000 hrs at L70, Operating Temperature:-10 TO +45 DEG.C; Input Supply Voltage Range:140-270 V, Frequency :50-60 HZ; Internal Surge Protection:3 KV; Protection : Reverse Polarity, Open and Short Circuit. DRIVER SAFETY REQUIREMENT STANDARDS :IS 15885-2-13, TEST REPORT TO BE SUBMITTED; PHOTO BIOLOGICAL SAFETY NORMS: IS 16108, TEST CERTIFICATE TO BE SUBMITTED; CERTIFICATION: LM 79 FOR LUMINAIRE LM 80 FOR LED SOURCE. | 500 | Nos
558 | 558 | Supply, Installation, testing and erecting of reccess mounted 1ftX1ft 18-20W. clean room Fixture made of MS powder coated white after phosphochromate treatment and High quality polycarbonate opal diffuser.High efficiency long life LEDs with lumen efficacy of >90 lm/W with system lumen 1620. Powered by an integral, Isolated, SELV Output electronic LED driver (SMPS based constant current supply) with Output Short-circuit protection, Surge protection. CCT 5700, CRI>80, THD<10 Percentage , PF>.95, Lumen Package>3200Lm(Fixture Efficacy), IP65, IK05.Life class of 50,000 hrs at L70, Operating Temperature:-10 TO +45 DEG.C; Input Supply Voltage Range:140-270 V, Frequency :50-60 HZ. DRIVER SAFETY REQUIREMENT STANDARDS :IS 15885-2-13, DRIVER PERFORMANCE REQUIREMENTS: IS 16104, PHOTO BIOLOGICAL SAFETY NORMS: IS 16108, CERTIFICATION: LM 79 FOR LUMINAIRE LM 80 FOR LED SOURCE. | 350 | Nos.
559 | 559 | Supply, Installation, testing and erecting of Heavy duty bulkhead reccess or surface type lighting fixture (ramp light) 9-10W IP-66 made up of pressure die-cast aluminium housing and Polyster Powder coated die cast aluminium with High quality polycarbonate diffuser in opal finish for glare free light distribution.High efficiency long life LED module with SMD LED package mounted on MCPCB with lumen efficacy of >95 lm/W with system lumen 950. Powered by integral electronic LED driver with APFC with low THD Output short/open circuit Protection. CCT 5700, CRI>80, System Efficacy>90Lm/W, THD<15 Percentage , PF>.95, IP66,IK 10, Life class of 50,000 hrs at L70, Operating Temperature:-10 TO +45 DEG.C; Input Supply Voltage Range:140-270 V, Frequency :50-60 HZ. DRIVER SAFETY REQUIREMENT STANDARDS :IS 15885-2-13, TEST REPORT TO BE SUBMITTED; DRIVER PERFORMANCE REQUIREMENTS: IS 16104, TEST REPORT TO BE SUBMITTED; PHOTO BIOLOGICAL SAFETY NORMS: IS 16108, TEST CERTIFICATE TO BE SUBMITTED; CERTIFICATION: LM 79 FOR LUMINAIRE LM 80 FOR LED SOURCE.HEXAFT10WLED857SSYMBOPC | 80 | Nos.
560 | 560 | Supplying and erecting LED indoor fittings with LEDs of wattage 0.2 Watt to 0.5 Watt assembled on single MCPCB, with housing used as a heat sink shall be made of thick sheet Steel conforming to IS: 513/CRCA polyester powder coated and high U.V. and corrosion resistance with diffuser and/or Polycarbonate optics with company mark/name 120 to 300 V,Power Factor more than 0.9, THD < 10 Percentage , CCT 4000 K to 6500K, Uniformity ratio >0.7, Luminaire efficiency> 85 lumens/watt , LED driver efficiency > 85 Percentage CREE / OSRAM / PHILIPS Lumileds / NICHIA / SEOUL/Bridgelux(U.S.A.) make LED used for luminaire. (Each fitting required LM-79 and LM-80 Certificates) (D) 20-22 Watts, Surge - 4KV,IP-20,Cat-lll, 4 Feet. | 3900 | Nos.
561 | 561 | Supplying and erecting LED Type Aviation light fixture with lamp and ballast complete to be fixed with required mounting arrangement with necessary hardware/materials etc and control box having auto timer and flickering circuit meeting parameters of AAI. Complete assembly should be IP65 or above in weather proof enclosures. | 1 | Nos.
562 | 562 | STREET LIGHT Supplying and erecting LED street light / Flood light fittings with High power White LEDs wattage of 1Watt and above assembled on single MCPCB, efficiency more than 130 lm/w and corrosion free High pressure die cast aluminum housing with smooth finish powder coated and heat sink extruded aluminium with diffuser and Polycarbonate optics/ lenses with company mark/name engraved or embossed 120 to 300 V,Power Factor more than 0.95, THD < 10 Percentage , CCT 5000 K to 5700K, Uniformity ratio >0.45, Luminaire efficiency> 85 lumens/watt . LED driver efficiency > 85 Percentage . CREE / OSRAM / PHILIPS Lumileds / NICHIA / SEOUL/ BridgeLux (U.S.A.) make LED used for luminaire. ( Each fittings required LM-79 and LM-80 certificates) (D) Post Top Lantern LED fitting comprises of Copper dust finish cast aluminum spigot and spun aluminum canopy fixed with opal polycarbonate, pipe arrangement for vertical mounting,open construction driver and accessories wired upto terminal block.cat-iii (a) 40W | 50 | Ea.
563 | 563 | Supplying and erecting LED street light / Flood light fittings with High power White LEDs wattage of 1Watt and above assembled on single MCPCB, efficiency more than 130 lm/w and corrosion free High pressure die cast aluminum housing with smooth finish powder coated and heat sink extruded aluminium with diffuser and Polycarbonate optics/ lenses with company mark/name engraved or embossed 120 to 300 V,Power Factor more than 0.95, THD < 10 Percentage , CCT 5000 K to 5700K, Uniformity ratio >0.45, Luminaire efficiency> 85 lumens/watt . LED driver efficiency > 85 Percentage . CREE / OSRAM / PHILIPS Lumileds / NICHIA / SEOUL/ BridgeLux (U.S.A.) make LED used for luminaire. ( Each fittings required LM-79 and LM-80 certificates) (A) Street Light (IP-65), Surge -4KV,(d) above 36 to 48 watts,cat-iii | 80 | Ea.
564 | 564 | Supplying and erecting LED street light / Flood light fittings with High power White LEDs wattage of 1Watt and above assembled on single MCPCB, efficiency more than 130 lm/w and corrosion free High pressure die cast aluminum housing with smooth finish powder coated and heat sink extruded aluminium with diffuser and Polycarbonate optics/ lenses with company mark/name engraved or embossed 120 to 300 V,Power Factor more than 0.95, THD < 10 Percentage , CCT 5000 K to 5700K, Uniformity ratio >0.45, Luminaire efficiency> 85 lumens/watt . LED driver efficiency > 85 Percentage . CREE / OSRAM / PHILIPS Lumileds / NICHIA / SEOUL/ BridgeLux (U.S.A.) make LED used for luminaire. ( Each fittings required LM-79 and LM-80 certificates) (B) (d) Flood Light (IP-65), Surge -4KV (d) above 100 to 120 watts Cat-lll | 10 | Ea.
565 | 565 | Supplying and erecting LED street light / Flood light fittings with High power White LEDs wattage of 1Watt and above assembled on single MCPCB, efficiency more than 130 lm/w and corrosion free High pressure die cast aluminum housing with smooth finish powder coated and heat sink extruded aluminium with diffuser and Polycarbonate optics/ lenses with company mark/name engraved or embossed 120 to 300 V,Power Factor more than 0.95, THD < 10 Percentage , CCT 5000 K to 5700K, Uniformity ratio >0.45, Luminaire efficiency> 85 lumens/watt . LED driver efficiency > 85 Percentage . CREE / OSRAM / PHILIPS Lumileds / NICHIA / SEOUL/ BridgeLux (U.S.A.) make LED used for luminaire. ( Each fittings required LM-79 and LM-80 certificates) "F ) Bollard LED fittings mounted on 60 cms high rotomoulded LLDPE pillar duly grouted on a concrete base by means of four nos of M8 X 75 mm studs with necessary base ring. (a) 8 W,680 Lumens, Surge -2KV Cat-lll | 10 | Ea.