## Sheet1
Re-wiring of Sector-07.xlsx
1 | S/F LED Bulkhead luminaire,10W LED, Graphite grey (RAL7024) powder coated pressure die-cast aluminium alloy housing. Diffused polycarbonate held with a silicon gasket. Fins provided on aluminium housing for better thermal management. LEDs are mounted on pressure Die-cast aluminium housing, Colour Temp. - 5700°K ±300°K, Power factor ≥ 0.95, THD <10% and inbuilt constant current driver up to 5kV surge protection. The luminaire is complete with all accessories wired up to a terminal block. PG7 Cable entry provided for to ensure better ingress protection. Degree of protection: IP65 complete all as specified and directed by EIC. | Each | 144
Make : Bajaj , Product code - 112334, BIBWP 10W LED or in philips, crompton
greaves
2 | S & F Building Security light fittings LED light with Lumen output 2100lm(System Lumens) with IP66 and wattage not more than 25W,color temperature 5700k, CRI>70, life 50000 burning hours as per LM79 & LM80 applicable for LEDS with secondery lenses and in built 5KV surge protection, 230V±10%AC,50-60Hz,P.f>0.95, Housing in Die cast aluminum, with protecting bowl in Polycarbonate bowl , Pole arm dia of 48mm, UL certified and CE,ROHS compliancemounting on wall and including GI pipe bracket made out of 40mm bore GI pipe light grade 1.5m long fixed with two sets of clamps made of MS flat iron 30x5mm, nuts bolts and washers and painting with two coats of aluminium paint over a coat of red oxide primer complete complete all as specified and directed by EIC. Make : Bajaj , Product code - 169708, BRLEP 25 W LED or in philips, crompton greaves | Each | 54
3 | 35 W , Well Glass High Bay LED light fixture with driver complete , cable entry from side,of Wipro make, Cat. No. | nos. | 150
4 | 36 W , square or circular or bracket LED down light fixture with driver complete , cable entry from side,of Wipro make, Cat. No. | nos. | 1
5 | 250W Area Fllod light fixtures from shed for surrounding Area | nos. | 1
6 | S & F Surface mounting LED slim circular down lighter with high efficiency LEDs & glare free opal diffuser fitting, range 10 to 12 W LED .Make: Bajaj/Philips/Wipro/Havells/Crompton/Hallonix/HPL | No | 120
7 | S & F High efficient LED street light with die cast aluminium housing ,reflector and enclosed with toughened glass, range 15 to 18 W LED .Make: j/Philips/Wipro/Havells/Crompton/Hallonix/HPL. Mounting shall be made with bracket made of 32 mm G.I Pipe medium grade of good quality and with | No | 40