## Sheet1
a) | 30W 2x2 - Supply of 30W, Recess mounted IP20 LED 2x2 Feet luminaire having greater than 3600 lm system output-120 lm/w system efficacy. Luminaire shall be made up of CRCA powder coated housing. Driver shall be fixed inside the housing only, no separate drier with wiring will be acceptable. Luminaire shall have Optical Grade High Efficiency Translucent Optical compartment for very high efficiency with minimum glare. Optical compartment shall have Unique HET diffuser for wider and uniform distribution. LM 80- 08 compliant, ANSI rated LEDs from reputed makes such as Nichia, Japan / Cree, USA / Citizen Japan should be provided. Luminaire shall have CCT 5700K ±350K. Luminaire shall use multiple LEDs of less than 0.5W Class for better diffusion and heat management. The LED shall be compliant with LM80-08 standard with Useful L70 life (L70 B10 or L70 B50 not acceptable) of 50000 Hrs (Complete LM 80 test report for LED should be submitted). The LEDs used in luminaire should be McAdam Step 5 standard Rated LED with CRI of Minimum 80. LEDs used must be tested as per EN62471 for Photobiological Safety of humans and Report of the same from LED Manufacturer shall be submitted. Driver shall be multi stage Constant Current Constant Voltage with voltage range of 150-270V AC. Output voltage of driver should be complied | Nos. | 250
b) | 12W Downlighter - Supply of 12W, Recess mounted IP20 LED Circular Downlighter luminaire having greater than 1200 lm system output-100 lm/w system efficacy.. Luminaire shall be made up of Die Cast powder coated housing with integral Fins. Driver shall be fixed with housing of the fixtures only, no separate driver with wiring will be acceptable. Luminaire shall have Optical Grade High Efficiency Translucent Optical compartment for very high efficiency with minimum glare. Optical compartment shall have Unique HET diffuser for wider and uniform distribution. LM 80-08 compliant, ANSI rated LEDs from reputed makes such as Nichia, Japan / Cree, USA / Citizen Japan should be provided. Luminaire shall have CCT 5700K ±350K. Luminaire shall use multiple LEDs of less than 0.5W Class for better diffusion and heat management. The LED shall be compliant with LM80-08 standard with Useful L70 life (L70 B10 or L70 B50 not acceptable) of 50000 Hrs (Complete LM 80 test report for LED should be submitted). The LEDs used in luminaire should be McAdam Step 5 standard Rated LED with CRI of Minimum 80. LEDs used must be tested as per EN62471 for Photobiological Safety of humans and Report of the same from LED Manufacturer shall be submitted. Driver shall be multi stage Constant Current Constant Voltage with voltage | Nos. | 300
c) | LED 4ft. 18 Watt ( Equivalent to. Wipro cat No D53206500K ) | Nos. | 10
d) | Hanging Light 40 Watt ( Equivalent to Wipro cat No. LM 34-501-xxx-57-DD) | Nos. | 7
e) | 5 watt / mt. 50/50 LED Strip Light With Driver (Equivalent to Wipro cat No. D45040 4000K ) | Mtr. | 100
f) | 9Watt Spot Light ( Equivalent to Wipro cat No D 120940) | Nos. | 70
g) | 20W Wall Mounted Decorative Light Phillips 31425 Muziris Singale head Wall Light ( Equivalent to Phillips Bronze E27 Base ) | Nos. | 30