## Table 2
Annexure
LED flood light Luminaire
1.1 Design Specifications
S.NO | Particulars | Specification | Compliance Yes / No
1 | Power Supply | Single phase 230 V  10 % ac, 50Hz
2 | Lamp type | Integral LED flood light fitting
3 | Make | PHILIPS /CG/Lighting technologies/OSRAM/IGUZZINI/ENDO/ TRILUX/K- LITE /TRILUX /WIPRO /DISANO /HALONIX /SCHREDER
4 | Wattage | 150W (Up to 10% variation on the higher side is also acceptable)
5 | Operating voltage range | 200 – 270V
6 | THD | <10%
7 | Surge Protection | against 5kV
8 | Beam angle | 60O
9 | Mounting Type | wall mounting
10 | Degree of protection | IP-65
11 | Luminaire efficacy | 90 lm/W or higher
12 | CRI | 70 or higher
13 | Optics | 1) Suitable for symmetrical down lighting
14 | Color Temperature | Cool white, 5700K or higher
15 | Luminaire body material | Metal body like high-pressure, die-cast aluminum
16 | Earthing | As per standard
17 | Ambient temperature | 45 OC or higher
18 | Terminal box | suitable for Loop in –loop out connections for paralleling multiple fittings
19 | Standards | As per relevant BIS/International standards
20 | Guarantee | 24 Months
General Terms and Conditions
1. Bidder should submit the datasheet furnishing all the detailed specifications of offered
item along with the offer
2. All items shall be completely pre-wired, tested and delivered in good working condition.
3. All items shall be guaranteed for a period of minimum 24 months from the date of supply against all manufacturing defects.
4. All items shall have a unique serial no imprinted on it.
The Above specificatons please clearly mention Yes / No / Any deviasion.
Note: If any deviasion then the tender is rejected