## Sheet1
SECTION 5 - BILL OF QUANTITES
LIGHTING
Item No |  | Sub-Heading | Description | Unit | Qty | Unit Rate (Rs) in figures | Unit Rate (Rs) in words | Amount Rs. | REMARK
F15.1600 |  | Lighting | LIGHTING |  |  |  |  | 0
F15.1601 |  | Lighting | Supply, Installation, Testing and Commisioning of Battern Luminaries 1X 34W LED Fixture, IP 65 with -Surface mounting arrangement on wall or ceiling - Single piece channel construction made of powder coated CRCA white sheet steel Refer Technical Specification for requirements. | Nos | 1200 |  |  | 0 | PRODUCT NOT AVAILABLE IN CRCA
F15.1602 |  | Lighting | Supply, Installation, Testing and Commisioning of Battern Luminaries 1X 34W LED Fixture with self contained battery power pack, IP 65 with -Surface mounting arrangement on wall or ceiling - Single piece channel construction made of powder coated CRCA white sheet steel Refer Technical Specification for requirements. | Nos | 600 |  |  | 0 | NA
F15.1603 |  | Lighting | Supply, Installation, Testing and Commisioning of Battern Luminaries 1X 30W LED Fixture with , IP 65 with -Recessed mounting arrangement (IP20) on wall or ceiling Refer Technical Specification for requirements. | Nos | 480 |  |  | 0 | PRODUCT NOT CLEAR( IP65 OR IP20)
F15.1604 |  | Lighting | Supply, Installation, Testing and Commisioning of Battern Luminaries 1X 30W LED Fixture with , IP 65 with self contained battery power pack -Recessed mounting arrangement (IP20) on wall or ceiling Refer Technical Specification for requirements. | Nos | 250 |  |  | 0 | NA
F15.1605 |  | Lighting | Supply, Installation, Testing and Commisioning of Battern Luminaries 1X 41W 2'X2' LED Fixture, IP 65 with -Recessed mounting arrangement (IP40 from above & IP20 from below) on wall or ceiling Refer Technical Specification for requirements. | Nos | 330 |  |  | 0 | PRODUCT NOT CLEAR( IP65 OR IP20)
F15.1606 |  | Lighting | Supply, Installation, Testing and Commisioning of Battern Luminaries 1X 41W 2'X2' LED Fixture with self contained battery power pack, , IP 65 with -Recessed mounting arrangement (IP40 from above & IP20 from below) on wall or ceiling Refer Technical Specification for requirements. | Nos | 190 |  |  | 0 | NA
F15.1607 |  | Lighting | Supply, Installation, Testing and Commlsioning of 1000W Metal Halide Floodlight lighting Fixtures for bay areas,local panel board. Refer Technical Specification & drawings for requirements. | Nos | 235 |  |  | 0
F15.1608 |  | Lighting | Supply, Installation, Testing and Commlsioning of 1X2W Emergency Exit lighting Fixtures, IP30 with self contained battery power pack. Refer Technical Specification & drawings for requirements. | Nos | 600 |  |  | 0
F15.1900 |  | Lighting | LIGHTING |  |  |  |  | 0
| F15.1900.1 | Lighting | Supply of LED based Flood light, housing made up of pressure die least aluminum Alloy with effective thermal management.sturdiness. The fixture should have a minimum system efficacy of 110 lumen/Watt and a minimum system lumen output of 45000 lumens and maximum system wattage of 400 Watts.The fixture shall have a CRI of minimum 70. The fixture shall be designed for a system life or 50,000 hours @70% lumen maintenance. Ingress Protection of IP66 (lamp and gear Compartment)and IK protection of IK08.The fixture driver should have an operating voltage range of 140-270 V, and wide operating temerature -40degC to 50degC surge protection of >=10KV, PF >0.9 and THD<10%.The fixture should comply with the parameters as per IS10322.LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters | Nos | 36 |  |  | 0 | HLFLD-ML06-400-CWL-HL1 with 10KV SPD
F1.500 |  | Lighting | INDOOR LIGHTING |  |  |  |  | 0
F1.501 |  | Lighting | Supply, installation, Testing and commissioning of batten luminaries 1x34 W LED Fixture, IP 65 with - Surface mounting arrangement on wall or ceiling - Single piece channel construction made of powder coated CRCA white sheet steel Refer Technical Specification for requirements | Nos | 90 |  |  | 0 | NA
F1.502 |  | Lighting | Supply, installation, Testing and commissioning of batten luminaries 1x34 W LED Fixture with self contained battery power pack, IP 65 with - Surface mounting arrangement on wall or ceiling - Single piece channel construction made of powder coated CRCA white sheet steel Refer Technical Specification for requirements | Nos | 40 |  |  | 0 | NA
F15.1800 |  | High Mast | HIGH MAST |  |  |  |  | 0
| F15.1800.1 | High Mast | Supply & installation of Galvanized steel high mast lighting system 60 meter high, in two section, 3 mm section thickness, top dla 150 mm, bottom dia 540 mm, with stainless steel 2 wire rope system and its accessories , suitable for loading 11 nos 210W LED lights | Nos | 1 |  |  | 0