## Sheet1
TECHNIC L SPECIFIC TION FOR LED FLOOD LIGHT of - 120 to 150 Watts
Total Quantity = 235 Nos
Sl. No | Parameters | Values | Complaince/ Remarks
1 | Input voltage | 140V to 270 V
2 | LDE lamp efficacy | Equal or greater than 110 lumens/watt
3 | Energy efficiency Lable | A grade
4 | Power factor | >0.95
5 | Life period | Equal or greater than 40,000 hours
6 | Rated watt | 120W to 150 W (cool day white)
7 | Luminous flux | Equal or greater than 13200 lumens (Test certificate to be submitted)
8 | Working Humidity | 10% to 90%
9 | Colour Temperature | Equal or greater than 5700K (Test certificate to be submitted)
10 | Ingress protection and IK rating | IP 65/IP 66 and IK Rating> IK 05 as per relevantIS/ IEC standard (Test certificate to be submitted)
11 | Total harmonic distortion (THD) | < 10% (Test certificate to be submitted)
12 | Colour rendering index | Equal or greater than 70
13 | Working Temperature | 20 deg to 45 deg C
14 | Average lighting/ beam angle | Equal or greater than 170 deg
15 | Lamp starting time | Not more than 0.5 sec
16 | Protection | Over Load, Over Current, Short Circuit, high voltage and Surge Protection
17 | System power efficiency | > 95 % (Test certificate to be submitted)
18 | Luminary Casing | Pressure die cast Aluminum with toughened glass cover and water proof fixture
19 | LED thermal management | LED shall be mounted on heat sink conductive aluminum with fins to dissipate the heat to ambient air
20 | Pole entry/ Retro fitting | Suitable for fixing in existing high mast with suitable bolt & nut
21 | Warranty | 1Years
22 | Driver board | Details shall be given for getting spare or vendor must ensure for providing driver board after warranty period is over