## BOQ
SR.NO | DESCRIPTION | UNIT | QTY | RATE- EACH | TOTAL
12 | Supply, Erection, Testing and commissioning of 1x18W LED fitting with 4 feet long LED tube complete, as per detailed technical specification. | Nos. | 500
34 | Supply, installation, testing & commissioning of indoor type LED Luminiaries 32 Watt, 2’ x 2’ size panel fitting, recess mounting type,complete with opel diffuser cover,constant current driver and all other accessories,as per technical specifications. | Nos. | 100
35 | Supply, installation, testing & commissioning of LED 2 x 18 Watt weather proof tube light fitting,as per technical specifications. | Nos. | 500
42 | Supply installation testing commissioning of decorative twin wall light fitting with 7 Watt x 2 LED bulb with glass cover decorative LED wall fitting. | Nos. | 40
45 | Supply,installation,testing and commissioning of LED Flood light fitting 100 Watt, IP 65 with fixing arrangement,as per technical specifications. | Nos. | 100
50 | Supply, Erection, Testing and commissioning of 200 Watt Flood LED Light fitting IP 65 protection,as per technical specifications. | Nos. | 100

## Specification
Item No
12, 34, 35, 50 | LED Light fittings: LED Light fitting SOR Item No. 12,34,35,45,50 should be as per guidelines from WR/CCG/SPECIFICATION/P/001(Rev-01)-2018. The technical specification is as follows:
| S.N . | Description of Parts | Details Specification
| 1 | Housing (Indoor fittings) | 1. Housing shall be made of CRCA powder coating / aluminum body. 2. The entire housing shall be having IP 20 protection for indoor application as per IEC60529.
| 2 | Front cover (Indoor fittings) | 1. All indoor light fittings shall be provided with polycarbonate / high efficiency Lumio diffuser, of sufficient strength under the LED chamber to protect the LED & luminaries.
| 3 | Housing (Outdoor fittings) | 1. Housing shall be made of 1.6mm thick sheet Steel confirming to IS 513 (Grade 0) or aluminum die cast having high conductivity preferably to grade 5000 with corrosion resistant powder coating. 2. The entire housing shall be dust and water proof having IP 65 protection for outdoor application as per IEC60529. 3. Housing of weather proof fittings for PF cover sheds may be of aluminum /FRP.
| 4 | Front cover (Outdoor fittings ) | 1. All outdoor light fittings shall be provided with toughened glass of sufficient strength under the LED chamber to protect the LED & luminaries. 2. Cover for 40W & below street light fittings may be of polycarbonate.
| 5 | Manufacturer’s name / logo | 1. Manufacturer’s name / logo & technical details shall be available on each fitting. 2. Each fitting shall have a distinct marking so as to facilitate
Item No
the traceability till the end of life (stickering is not acceptable).
| 6 | LED lamp make | 1. LED lamps of NICHIA/ CREE/ OSRAM/ SEOUL/ PHILIPS LUMILEDS/ SAMSUNG make shall be used for the purpose.
| 7 | LED lamp | 1. The working life of the LED lamp shall be more than 50,000 hours and shall be suitable for continuous operation of 24 hours. 2. Colour temperature of the proposed white colour LED shall be between 5700K – 6500K. 3. LED Tj / junction temperature shall not go beyond 800C & LED Tc/ surface temperature shall not go beyond 550C.
| 8 | LED driver | 1. The driver card shall withstand 440V normal & 3 KV ±3% surge protection. Driver shall be isolated type. 2. Input voltage range within 140Vrms to 270Vrms. Operating input voltage 240Vrms.
| 9 | LED Luminaire | 1. Power factor of complete fitting shall be more than 0.95. 2. Color rendering index CRI ≥ 75. 3. Variation in illumination level shall be ±2% is allowed in input voltage range from 170VAC to 270VAC.
| 10 | Efficacy (Lumen / Watt) | 1. Efficacy of LED luminaire/system shall be minimum 100 lumens/watt or more (including power consumption by driver).
| 11 | Warranty | 1. Warranty of the Luminaire shall be five years. 2. The supplier shall provide “In the field service support” during warranty period. 3. Security Deposit will be released after expiry of warranty period.
| 12 | Certificates to be submitted | 1. LM - 79 test certificate from NABL/UL approved laboratory. 2. LM - 80 test certificate by the manufacturer & LED Technical datasheet. 3. OEM’s Test report / certificates – confirming to housing material, surface temperature, junction temperature, make of LED used, input & output wattage in full load, IP-20 or IP-65., driver’s efficacy.
1) The firm shall submit OEM’s documents / reports for confirmation of parameters like LED Luminaire, LED lamp make, wattage, Efficacy (Lumen / Watt), Warranty.
2) A factory inspection, if asked by Railway authority, shall be carried out with the Consignee.
3) A sample shall be got approved from the Dy. CEE/C/CCG or conerned Railway authority.
LED fittings such as decorative wall fittings, reading light / night light / foot light / spot light fittings, bubs/ lamps, down lighters, garden / Par lights / wall washer / customized fittings and other such type of LED fittings will not require compliance of above specifications and warrantee period of such fittings shall be one year only.
42 | Wall Decorative Twin LED fitting: The Price shall cover Supply, erection, testing and commissioning of the work. The fitting shall be Twin decorative type, having each of suitable for providing 7 Watt LED bulb 02 Nos. with glass covered in each bulb or LED fitting of 14 watt capacity decorative type. The fitting shall be supplied with 02 Nos. of LED 7W bulb. The wall fitting shall be decided by SSE/C/P/NDB.