## Sheet1
Annexure - TD
(a) LED Type Flood Light Fixture
S. No | Technical Parameters | Technical specification requirement | Technical details of fitting offered | Remarks
1 | Efficiency of LED light fitting(efficacy) | Minimum 95 Lumens / Watt
2 | Life of LED light fitting | Not less than 50000 burning hrs.
3 | Approved Make for LED | Nichia / Cree / Osram / Philips (Lumiled) / Sharp/Seoul. (See note below)
4 | Color Rendering Index (CRI) | > 70%.
5 | Total Harmonic Distortion (THD) | Less Than 10%
6 | Surge Protection | Shall be provided confirming to relevant IS standards/IEC 61643-II class- 2 & EN 61643-II type -2. 4KV (Internal) + 10 KV (External) for Flood light
7 | Total Power consumption | Not more than 110% of the rated capacity of LED Light
8 | Type of Housing & Driver | High pressure die cast Aluminum / standard alloy with extruded aluminum heat sink. Driver should be potted type.
9 | IP category | IP 65 or Higher
10 | Optic Cover/ Diffuser | Suitable optics with Heat resistant toughened glass with gasket.
11 | Standard Accessories | Mounting bracket for aiming adjustment.
12 | Suitability | For installation on existing High Mast
13 | Power factor | Equal to 0.95 or more
14 | Labeling /Identification Mark | Manufactures Name /Logo engraved / embossed on housing /body or Name /Logo on aluminum plate labels or Name /Logo printed on housing /body
15 | Warranty Period | Five Years warranty from actual Date of Completion of Work on complete luminaire including driver /Control gear, LED, all accessories etc.
16 | Confirmation for submission of Test Reports /Certificates & Documents in English Language during execution in case of award. | 1.Type test certificate from NABL/reputed accredited test lab. (LM-79 Report) etc.
2.Other test certificates/supporting documents for complying the above specifications. (LM-80 for LED & photo biological report for Eye safety) etc.
3.An undertaking from fitting manufacturer regarding confirmation about use of said make LED's in their fitting.