## Sheet1
LED FITTINGS
1.1 The LED luminaires shall comply with the relevant IS specifications with up to date amendments and meet the Technical parameters as below:
S.No. | Technical Parameters | Recommended requirement | Offering | Remark
1 | Efficiency of LED light fitting (Efficacy) | Min 120 Lumens / Watt
2 | Life of LED light fitting | Not less than 50000 burning hours
3 | Approved make for LED | Nichia/Cree/Osram/Phillips(Lumiled)/Sharp/Seoul. (See Note Below)
4 | CRI (Colour Rendering Index) | Min 80 for indoor applications and Min 70 for outdoor applications.
5 | THD (Total Harmonic Distortion) | Less than 10%
6 | Type of Housing | Extruded aluminum / Standard alloy housing for indoor applications. High pressure die cast aluminium / Standard alloy for outdoor applications.
7 | IP Category | IP 20 or higher for indoor applications and IP 65 or higher for outdoor applications.
8 | Surge Protection | Shall be provided conforming to relevant IS standard / IEC 61643-II class — 2 & EN 61643-II Type-2.
9 | Labeling / identification Mark | Manufactures Name / Logo engraved / Embossed on housing / body or Name / Logo on aluminium plate Labels or Name / Logo printed on housing / body.
10 | Warranty period | 5 years warranty from actual date of completion of work on complete luminaire including driver / control gear, LED, all accessories etc.
11 | Power Factor | Equal to 0.95 or More.
12 | Total Power consumption of fitting. | Not more than 110% of rated capacity of LED light.
Note:
1.An Undertaking shall be submitted from fitting manufacturer regarding confirmation
about use of said make LED's in their fittings.
2.The Test reports such as LM 79 and LM 80 of the Luminaire from Accredited