## Sheet1
Project - Dehradun Airport
Technical Comparative Sheet for Lights Fixtures
S. No. | Boq Sno | Parameters | ACIL- As per BOQ & TS
1 | 288 | 18W Recessed LED Down lighter
|  | Make of LED | Nichia/Cree/Philips(Lumiled)/ Osram/ Sharp/ Seoul
|  | Model No. | Trilux Ambiella Plus IND G3 LED1530-840 ET / Wipro CRDL11R023HP40DE / Philips DN395B LED20S-4000 PSU WH or equivalent
|  | Wattage of Light | 18W
|  | Output Lumens (Lm) | 1800
|  | Lumens/watt | 100lm/W
|  | CRI | >80
|  | Power factor | >0.95
|  | Diode type | SMD( Surface mounted diode)
|  | Color temperature | 4000
|  | Driver Efficiency | 85%
|  | THD (Total Harmonic Distortion) | <=10%
|  | IP Rating | IP20
|  | Life span (in hrs) | 50000 @ L70B50
|  | Internal Surge protection | 2.5KV
|  | Housing Material | Pressure die cast aluminum with translucent PMMA diffuser.
|  | Certification | IS 10322/EMC/ EMI
|  | Driver leakage current Certification | IEC 60598
|  | Beam Angle | 120°
|  | Minimum Continous operation | 12 hours
|  | Luminaire testing certification | LM-79, LM-80 and third party testing certificates
|  | Output Voltage Ripple | <=3%
|  | Thickness of body of light fixture | 22SWG
|  | Thickness of steel reflectors | 20SWG
|  | Warranty for luminaire, driver/control gear, LED & all accessories | 5 Years from date of handling
2 | 289 | 36W LED Recessed 600m X 600m
|  | Make of LED | Nichia/Cree/Philips(Lumiled)/ Osram/ Sharp/ Seoul
|  | Model No. | Trilux Enterio IND M73 OA LED 3600-840 ET / Wipro CRCO10R036HP40G1DE / Philips RC380B LED34S-4000 G3 PSU OD or equivalent
|  | Wattage of Light | 36W
|  | Output Lumens (Lm) | 3600
|  | Lumens/watt | 100lm/W
|  | CRI | >80
|  | Power factor | >0.95
|  | Diode type | SMD( Surface mounted diode)
|  | Color temperature | <=4000
|  | Driver Efficiency | 85%
|  | THD (Total Harmonic Distortion) | <=10%
|  | IP Rating | IP20
|  | Life span (in hrs) | 50000 @ L70B50
|  | Internal Surge protection | 2.5KV
|  | Housing Material | White CRCA Powder coated
|  | Certification | IS 10322 & EMC/ EMI
|  | Driver leakage current Certification | IEC 60598
|  | Beam Angle | 120°
|  | Minimum Continous operation | 12 hours
|  | Luminaire testing certification | LM-79, LM-80 and third party testing certificates
|  | Output Voltage Ripple | <=3%
|  | Thickness of body of light fixture | 22SWG
|  | Thickness of steel reflectors | 20SWG
|  | Warranty for luminaire, driver/control gear, LED & all accessories | 5 Years from date of handling
3 | 290 | 12W LED Recessed Down lighter
|  | Make of LED | Nichia/Cree/Philips(Lumiled)/ Osram/ Sharp/ Seoul
|  | Model No. | Trilux Ambiella Plus IND G3 LED1000-840ET/ Wipro CRDL11R017HP40DE / Philips DN393B LED12S-4000 PSU WH or equivalent
|  | Wattage of Light | 12W
|  | Output Lumens (Lm) | 1200
|  | Lumens/watt | 100lm/W
|  | CRI | >80
|  | Power factor | >0.95
|  | Diode type | SMD( Surface mounted diode)
|  | Color temperature | 4000
|  | Driver Efficiency | 85%
|  | THD (Total Harmonic Distortion) | <=10%
|  | IP Rating | IP20
|  | Life span (in hrs) | 50000 @ L70B50
|  | Internal Surge protection | 2.5KV
|  | Housing Material | Pressure die cast aluminum with translucent PMMA diffuser.
|  | Certification | IS 10322/EMC/ EMI
|  | Driver leakage current Certification | IEC 60598
|  | Beam Angle | 120°
|  | Minimum Continous operation | 12 hours
|  | Luminaire testing certification | LM-79, LM-80 and third party testing certificates
|  | Output Voltage Ripple | <=3%
|  | Thickness of body of light fixture | 22SWG
|  | Thickness of steel reflectors | 20SWG
|  | Warranty for luminaire, driver/control gear, LED & all accessories | 5 Years from date of handling
4 | 291 | 36W Surface mount LED fitting
|  | Make of LED | Nichia/Cree/Philips(Lumiled)/ Osram/ Sharp/ Seoul
|  | Model No. | Trilux LED Batten D OTA LED 3600 CW ET / /NW L1200 FR / Wipro LE10-491-XXX57DE / Philips BN108C LED 40S PSU NW WH or equivalent
|  | Wattage of Light | 36W
|  | Output Lumens (Lm) | 3600
|  | Lumens/watt | 100lm/W
|  | CRI | >80
|  | Power factor | >0.95
|  | Diode type | SMD( Surface mounted diode)
|  | Color temperature | 5700-6500K
|  | Driver Efficiency | 85%
|  | THD (Total Harmonic Distortion) | <=10%
|  | IP Rating | IP20
|  | Life span (in hrs) | 50000 @ L70B50
|  | Internal Surge protection | 2.5KV
|  | Housing Material | CRCA
|  | Certification | IS 10322/EMC/ EMI
|  | Driver leakage current Certification | IEC 60598
|  | Beam Angle | 120°
|  | Minimum Continous operation | 12 hours
|  | Luminaire testing certification | LM-79, LM-80 and third party testing certificates
|  | Output Voltage Ripple | <=3%
|  | Thickness of body of light fixture | 22SWG
|  | Thickness of steel reflectors | 20SWG
|  | Warranty for luminaire, driver/control gear, LED & all accessories | 5 Years from date of handling
5 | 292 | 115W LED Industrial BAY
|  | Make of LED | Nichia/Cree/Philips(Lumiled)/ Osram/ Sharp/ Seoul
|  | Model No. | Trilux LBL 11500 ET / Wipro LH09-122-120/ Philips Maxoled BY415 LED90S WB FG PSU or equivalent
|  | Wattage of Light | 115W
|  | Output Lumens (Lm) | 11500
|  | Lumens/watt | 100lm/W
|  | CRI | >80
|  | Power factor | >0.95
|  | Color temperature | 4000-5700K
|  | Driver Efficiency | 85%
|  | THD (Total Harmonic Distortion) | <=10%
|  | IP Rating (Luminaire & Control Gearbox) | IP 65
|  | Life span (in hrs) | 50000 @ L70B50
|  | Internal Surge protection | 4KV
|  | Housing Material | Pressure die cast aluminum with translucent PMMA diffuser.
|  | Certification | IS 10322/EMC/ EMI
|  | Driver leakage current Certification | IEC 60598
|  | Beam Angle | 120°
|  | Minimum Continous operation | 12 hours
|  | Luminaire testing certification | LM-79, LM-80 and third party testing certificates
|  | Output Voltage Ripple | <=3%
|  | Thickness of body of light fixture | 22SWG
|  | Thickness of steel reflectors | 20SWG
|  | Warranty for luminaire, driver/control gear, LED & all accessories | 5 Years from date of handling
6 | 293 | 48W Round LED Down lighter
|  | Make of LED | Nichia/Cree/Philips(Lumiled)/ Osram/ Sharp/ Seoul
|  | Model No. | Trilux InperlaL G2 C07 BR25 4700-840 / Wipro LD-56-501-XXX-40-DE / Philips DN570B LED40S/840 PSEU-E CWH or equivalent
|  | Wattage of Light | 48W
|  | Output Lumens (Lm) | 4800
|  | Lumens/watt | 100lm/W
|  | CRI | >80
|  | Power factor | >0.95
|  | Color temperature | 4000
|  | Driver Efficiency | 85%
|  | THD (Total Harmonic Distortion) | <=10%
|  | IP Rating | IP20
|  | Life span (in hrs) | 70000 @ L80, 50,000 at L85
|  | Internal Surge protection | 2.5KV
|  | Housing Material | Die cast aluminum white powder coated
|  | Certification | IS 10322/EMC/ EMI
|  | Driver leakage current Certification | IEC 60598
|  | Beam Angle | 120°
|  | Minimum Continous operation | 12 hours
|  | Luminaire testing certification | LM-79, LM-80 and third party testing certificates
|  | Output Voltage Ripple | <=3%
|  | Thickness of body of light fixture | 22SWG
|  | Thickness of steel reflectors | 20SWG
|  | Warranty for luminaire, driver/control gear, LED & all accessories | 5 Years from date of handling
7 | 294 | 8W LED Recessed Circular Down lighter
|  | Make of LED | Nichia/Cree/Philips(Lumiled)/ Osram/ Sharp/ Seoul
|  | Model No. | Trilux Ambiella IND G3 LED 640-840 ET / Wipro CRDL11R013HP40DE / Philips DN 392BLED10S-6500 PSU WH or equivalent
|  | Wattage of Light | 8W
|  | Output Lumens (Lm) | 800
|  | Lumens/watt | 100lm/W
|  | CRI | >80
|  | Power factor | >0.95
|  | Diode type | SMD( Surface mounted diode)
|  | Color temperature | <=4000
|  | Driver Efficiency | 85%
|  | THD (Total Harmonic Distortion) | <=10%
|  | IP Rating | IP20
|  | Life span (in hrs) | 50000 @ L70B50
|  | Internal Surge protection | 2.5KV
|  | Housing Material | Pressure die cast aluminum with translucent PMMA diffuser.
|  | Certification | IS 10322/EMC/ EMI
|  | Driver leakage current Certification | IEC 60598
|  | Beam Angle | 120°
|  | Minimum Continous operation | 12 hours
|  | Luminaire testing certification | LM-79, LM-80 and third party testing certificates
|  | Output Voltage Ripple | <=3%
|  | Thickness of body of light fixture | 22SWG
|  | Thickness of steel reflectors | 20SWG
|  | Warranty for luminaire, driver/control gear, LED & all accessories | 5 Years from date of handling
8 | 295 | 15W/m Strip Light
|  | Make of LED | Nichia/Cree/Philips(Lumiled)/ Osram/ Sharp/ Seoul
|  | Model No. | Wipro LS06-015-120-WW-50 / Philips CAT NO.- LS152S LED8/WW L5000 IN Flexible Strip Light / Trilux LEDM Flexi Strip light 15W/M (In Meter) or equivalent
|  | Wattage of Light | 15W/m
|  | Output Lumens (Lm) | 1500lm/m
|  | Lumens/watt | 100lm/W
|  | Driver Efficiency | 85%
|  | THD (Total Harmonic Distortion) | <=10%
|  | IP Rating | IP20
|  | Life span (in hrs) | 50000
|  | Thickness of body of light fixture | 22SWG
|  | Thickness of steel reflectors | 20SWG
|  | Warranty for luminaire, driver/control gear, LED & all accessories | 5 Years from date of handling
9 | 296 | 75W LED Flood light
|  | Make of LED | Nichia/Cree/Philips(Lumiled)/ Osram/ Sharp/ Seoul
|  | Model No. | Trilux Combial 30-RB8R/7500-740 1G1W ET / Wipro LF19-931-060-40-DE / Philips BVP122 LED110 NW FLNB FG XTFC or equivalent
|  | Wattage of Light | 75W
|  | Output Lumens (Lm) | 7500
|  | Lumens/watt | 100lm/W
|  | CRI | >80
|  | Power factor | >0.95
|  | Color temperature | 4000
|  | Driver Efficiency | 85%
|  | THD (Total Harmonic Distortion) | <=10%
|  | IP Rating | IP65
|  | Life span (in hrs) | 50000 @ L80
|  | Internal Surge protection | 4KV
|  | Housing Material | Spotlight body of Die cast Aluminum Powder coated cover of non laminated safety glass (EN61140)
|  | Certification | IS 10322/EMC/ EMI & IEC62262(impact resistance)
|  | Driver leakage current Certification | IEC 60598
|  | Beam Angle | 120°
|  | Minimum Continous operation | 12 hours
|  | Luminaire testing certification | LM-79, LM-80 and third party testing certificates
|  | Output Voltage Ripple | <=3%
|  | Thickness of body of light fixture | 22SWG
|  | Thickness of steel reflectors | 20SWG
|  | Warranty for luminaire, driver/control gear, LED & all accessories | 5 Years from date of handling
10 | 297 | 110W LED Floodlight
|  | Make of LED | Nichia/Cree/Philips(Lumiled)/ Osram/ Sharp/ Seoul
|  | Model No. | Trilux Combial 40RB8R/12000-740 1G1W / Wipro LF20-132-060-40-DE / Philips BVP122 LED128 CW FLNB FG XTFC or equivalent
|  | Wattage of Light | 110W
|  | Output Lumens (Lm) | 12000lm
|  | Lumens/watt | >100lm/W
|  | CRI | >80
|  | Power factor | >0.95
|  | Color temperature | 4000
|  | Driver Efficiency | 85%
|  | THD (Total Harmonic Distortion) | <=10%
|  | IP Rating | IP65
|  | Life span (in hrs) | 50000 @ L70B50
|  | Internal Surge protection | 4KV
|  | Housing Material | Spotlight body of die cast aluminum Black Color powder coated
|  | Certification | IS 10322/EMC/ EMI & IEC62262(impact resistance)
|  | Driver leakage current Certification | IEC 60598
|  | Beam Angle | 120°
|  | Minimum Continous operation | 12 hours
|  | Luminaire testing certification | LM-79, LM-80 and third party testing certificates
|  | Output Voltage Ripple | <=3%
|  | Thickness of body of light fixture | 22SWG
|  | Thickness of steel reflectors | 20SWG
|  | Warranty for luminaire, driver/control gear, LED & all accessories | 5 Years from date of handling