## Table 1
Sl. No. | DESCRIPTION OF ITEM | UNIT | QTY
28 | SUPPLY AND FIXING OF LIGHT FIXTURE AND FAN
i) | 12-18W Surface Mounted LED Downlighter Low Height with system efficacy of minimum 110Lumens per watt ,Extruded aluminium housingwith PMMA Diffuser. Color Rendering Index Ra >80, Color Temperature of 5700K. BIS certified Inbuilt electronic Driver with Power Factor > 0.9, Total Harmonic Distortion <10%,Surge Protection 2KV, Life Class of 50,000 hours @L70 and in compliance to IEC Safety Standards. LM 79 and LM 80 reports to be submitted from a NABL accredited lab to verify above parameters. including connections with 1.5sq mm FRLS PVC insulated copper conductor single core cable etc. complete as required. | Nos | 300
HALONIX-HLDLS-R06-18CW
ii) | IP20 recessed mounted luminaire 2ft x2ft, 33-36W with min. system efficaccy minimum 110lumens / Watt with CRCA Housing Color Rendering Index Ra >80, Color Temperature of 5700K. BIS certified Inbuilt electronic Driver with Power Factor > 0.9, Total Harmonic Distortion <10%,Surge Protection 2KV, Life Class of 50,000 hours @L70 and in compliance to IEC Safety Standards. LM 79 and LM 80 reports to be submitted from a NABL accredited lab to verify above parameters. including connections with 1.5sq mm FRLS PVC insulated copper conductor single core cable etc. | Nos | 1200
HALONIX HLFPR22-03-36-CW-R
iii) | Supply & Fixing of of 10-12W Reccess Mounted LED Downlighter Low Height with system efficacy minimum 110lumens / Watt,Extruded aluminium housingwith PMMA Diffuser. Color Rendering Index Ra >80, Color Temperature of 5700K. BIS certified Inbuilt electronic Driver with Power Factor > 0.9, Total Harmonic Distortion <10%,Surge Protection 2KV, Life Class of 50,000 hours @L70 and in compliance to IEC Safety Standards. LM 79 and LM 80 reports to be submitted from a NABL accredited lab to verify above parameters. including connections with 1.5sq mm FRLS PVC insulated single core cable etc. complete as required. ( make and Model as List attached) | Nos | 585
HALONIX MODEL HLDLR-31-12-CW
iv) | IP20 recessed mounted luminaire downlighter, 15W with system efficacy minimum 110Lumens / Watt with CRCA Housing Color Rendering Index Ra >80, Color Temperature of 5700K. BIS certified Inbuilt electronic Driver with Power Factor > 0.9, Total Harmonic Distortion <10%,Surge Protection 2KV, Life Class of 50,000 hours @L70 and in compliance to IEC Safety Standards. LM 79 and LM 80 reports to be submitted from a NABL accredited lab to verify above parameters. including connections with 1.5sq mm FRLS PVC insulated single core cable etc. | Nos | 2000
HALONIX- HLDLR-31-15-CW
v) | Supply & Fixing of 9-10W IP 65 Bulk Head Luminaire with system efficiancy minimum 110 lumens per watt with PDC Housing. Color Rendering Index Ra >80, Color Temperature 5700K. BIS certified Inbuilt electronic Driver with Power Factor > 0.9, Total Harmonic Distortion <10%,Surge Protection 2KV, Life Class of 50,000 hours @L70 and in compliance to IEC Safety Standards. LM 79 and LM 80 reports to be submitted from a NABL accredited lab to verify above parameters.including connections with 1.5sq mm FRLS PVC insulated copper conductor cable etc. | Nos | 40
HALONIX-HLBH-04-10-CW
vi) | 30-40W IP 65 Street Lighting Luminaire with PDC Housing, System Lumen >100lm/w. Color Rendering Index Ra >80, Color Temperature 5700K BIS certified Inbuilt electronic Driver with Power Factor > 0.9, Total Harmonic Distortion <10%,Surge Protection 4KV internal and 10KV external, Life Class of 50,000 hours @L70 and in compliance to IEC Safety Standards. LM 79 and LM 80 reports to be submitted from a Govt accredited lab to verify above parameters with all accessories with connection with three core copper wire of suitable size | Nos | 160
HALONIX-HLSLD-09-30-CWL-R