## Sheet1
SR NO | ITEAMDESCRIPITION | QTY | UNIT
2300 | LIGHTING FIXTURES
2301 | Supply, Installation, connection and testing of following lighting fixtures with lamps sources,
suitable drivers / controlgears with the junction box provided for the point / cable wiring,
including supply of all hardware required for installation, labour and materials as per
specifications, drawings and directions of Engineer-in-charge.
For all recessed type light fixtures, Suitable Bottom mounting frames, brackets, chains,
wire ropes shall be provided alongwith the light fixture to match the false ceiling profile and
to achieve the total recessed type light fixture fixing arrangement with the false ceiling.
All lights indoor, outdoor, landscape, underwater etc. shall be provided with all complete
accessories including but not limited to backbox, connectors, power supply modules etc. for
complete installation.
5 Years of Replacement warranty shall be provided for All LED light fixtures
from Manufaturer.
2301.1 | 120W Symmetric, Wide Beam optics, SMD LED Highbay light fixture suitable to surfaced | 133 | Nos.
and suspended mounting with below specification.
Lumens output: 15600 lumens (130 Lumens/Watt)
Color temperature: 5700-6500 K
CRI: > 80
Ingress Protection - IP-65
Inbuilt Surge Protection
Operating Voltage range: 140V-270V
L70 - >50,000 hours
2301.2 | 38-40W, Symetric, Indoor LED batten (Integrated LED), suitable to surface mouting with | 26 | Nos.
below specification. Surface mounting.
Lumens output: 4000 lumens (>100 Lumens/Watt)
Color temperature: 5700-6500 K
CRI: > 80
Ingress Protection - IP-20
Inbuilt Surge Protection up
Operating Voltage range: 140V-270V
L70 - >50,000 hours
2301.3 | 38-40W, Symetric, outdoor LED batten (Integrated LED), suitable to surface mouting with | 97 | Nos.
below specification.
Lumens output: 4000 lumens (>100 Lumens/Watt)
Color temperature: 5700-6500 K
CRI: > 80
Ingress Protection - IP-65
Inbuilt Surge Protection up
Operating Voltage range: 140V-270V
L70 - >50,000 hours
2301.4 | 36W, 2' X 2" Recessed mounted LED light fixture with below specification | 18 | Nos.
Lumens output: 3600 lumens (>100 Lumens/Watt)
Color temperature: 5700-6500 K
CRI: > 80
Ingress Protection - IP-20
Inbuilt Surge Protection up
Operating Voltage range: 140V-270V
L70 - >50,000 hours
2301.5 | 15W, Round surface mounted LED light fixture, suitable for surface with below specification | 24 | Nos.
Lumens output: 1500 lumens (>100 Lumens/Watt)
Color temperature: >5700 K
CRI: > 80
Ingress Protection - IP-20
Inbuilt Surge Protection up
Operating Voltage range: 140V-270V
L70 - >30,000 hours
2301.6 | 70W, Street Light Fixture, suitable to mount on street light pole with below specification | 22 | Nos.
Lumens output: 7000 lumens (>100 Lumens/Watt)
Color temperature: >5700 K
CRI: > 80
Ingress Protection - IP-66
Inbuilt Surge Protection up
Operating Voltage range: 140V-270V
L70 - >50,000 hours
2301.7 | 45W, Street Light Fixture, suitable to mount on street light pole with below specification | 5 | Nos.
Lumens output: 4500 lumens (>100 Lumens/Watt)
Color temperature: >5700 K
CRI: > 80
Ingress Protection - IP-66
Inbuilt Surge Protection up
Operating Voltage range: 140V-270V
L70 - >50,000 hours
2301.8 | 18/20W, Bollard Type outdoor Light fixtures with post, 900 Lumens, IP65 protection CRI > 70, |  | UR/Nos.
pole suitable to mount on base plate. Color temperature 4000K. (Rates shall include civil
foundation requirements)
2301.9 | 150/160W, High power LED Flood Light Fixture, suitable for outdoor pole mounting. Installed | 11 | Nos.
on 12 meter pole with below specification.
Lumens output: 15000 lumens (>100 Lumens/Watt)
Color temperature: >5700 K
CRI: > 80
Ingress Protection - IP-66
Inbuilt Surge Protection up
Operating Voltage range: 140V-270V
L70 - >50,000 hours
2301.1 | 70W, High power LED Flood Light Fixture, suitable for outdoor installation with below | 16 | Nos.
specification.
Lumens output: 7000 lumens (>100 Lumens/Watt)
Color temperature: >5700 K
CRI: > 80
Ingress Protection - IP-66
Inbuilt Surge Protection up
Operating Voltage range: 140V-270V
L70 - >50,000 hours
2301.11 | 38W, 2' X 2" Recessed mounted CLEAN ROOM LED light fixture, bottom openable and with |  | UR/Nos.
below specification
Color temperature: >5700 K
CRI: > 80
Ingress Protection - IP-20
Inbuilt Surge Protection up
Operating Voltage range: 140V-270V
L70 - >50,000 hours
2302 | Supply, Installation, testing and commissioning of 4W LED Exit lighting unit with | 8 | Nos.
maintenance free battery suitable for 1 hour operation incase of power failure. With battery
charger operating on 240V AC supply including all labour and materials as per drawings,
standard specifications and directions of Engineer-in-charge.
2303 | Supply, installation, connection, testing and commissioning of Wall / M.S. channel mounted,
flameproof and weatherproof type lighting fixtures including transportation from owner's site
store to the place of erection and supply of all necessary hardware as per specifications,
drawings and directions of Engineer-in-charge (Supply of the required structural steel is
covered else where in the tender).All lighting fixtures shall be suitable for application in Zone #
1 & 2, Gas Group IIA, IIB, Temperature class T6 .
Construction - Cast Aluminum Alloy LM6 as per IS 2148, Epoxy finish. Installation - Through
M.S. clamp / bracket with fixing bolts, nuts and spring washers.
Ingress Protection - IP 65
Area Classification - Zone 1 & 2, Gas Group IIA & IIB, Temperature Class T6
a | 63W LED type,flame proof and weatherproof well glass light fixture | 6 | Nos.