## Sheet1
S.No. | Description | Unit | Total Station Qty.
A.05 | INDOOR LIGHTING AND FANS
5 | Supply, installation, testing & commissioning of LED light fittings including all accessories e.g. Driver, HPF condensers (surge protector), surface/recess mounting arrangement etc. including necessary supports, accessories and hardware as per specifications & as required at site and as below:
5.1 | Luminaries minimum specifications and requirements
a) | Luminaries should operate at +/- 6% voltage fluctuation for continuous use to comply to IEC. PF > 0.95 for EM circuits PF > 0.85 with capacitor.
b) | All the components including the internal wiring of the luminaries to be used shall be manufactured of material, which are of FR type. All luminaries shall be manufactured to relevant sections of IEC60598 or other approved international standards and the type tests for all luminaries shall be provided.
c) | All internal wiring within the lighting fixtures shall be heat-resisting cables.
Note: Lamp should have free replacement for one year from the date of Installation. The Date of installation shall be from the date of handing over the work to BMRCL.
5.1.1 | Supply, Installation, Testing & Commissioning of surface/suspended continuous LED Luminaries, made up of extruded Aluminum housing and CRCA heatsink with extruded PC diffuser. Luminaries should be with minimum system efficacy of 100Lumen/Watt and minimum system lumen output of 2600lm, maintained at 70% at the end of 50,000 burning hours. The luminaries should have CRI>80 and CCT of 6500K. Luminaries should withstand THD less than 10% and should have power factor > 0.90. Driver efficiency should be 85%. Luminaries should comply with all the required IEC standards and should operate in a voltage range of 140 to 270 volts AC. Similar To Philips Pureline Slim LED 75mm_down (75mmx1120mm) or approved equivalent Make. ( PUBLIC AREA, Platform area) | Nos. | 25310
5.1.2 | Supply, Installation, Testing & Commissioning of Trunking LED ,made up of extruded Aluminium body and acrylic cover. Luminaries should be with minimum system efficacy of 110 Lumen/Watt and minimum system lumen output of 4000, maintained at 70% at the end of 50,000 burning hours. The luminaries should have CRI>80 and CCT of 6500K. Luminaries should withstand THD less than 10% and should have power factor > 0.95 . Driver efficiency should be 85%. The luminaries should be IP 54 protected. Luminaries should comply with all the required IEC standards and should operate in a voltage range of 220 to 240 volts AC. Similar To Philips Optimus LED Trunking LL199X1XDLED40-6500 PSE OD WH or approved equivalent Make.(Platform edge) | Nos. | 6141
5.1.3 | Supply, Installation, Testing & Commissioning of surface/Conduit LED Batten Luminaries, made up of CRCA sheet with glossy PC diffuser. Luminaries should be with minimum system efficacy of 100Lumen/Watt and minimum system lumen output of 4000 maintained at 70% at the end of 40,000 burning hours. The luminaries should have CRI>80 and CCT of 6500K. Luminaries should withstand THD less than 10% and should have power factor > 0.95 . Driver efficiency should be 85% . Luminaries should comply with all the required IEC standards and should operate in a voltage range of 140 to 270 volts AC. Similar To Philips Endura LED Batten BN108C LED 40S PSU CDL WH or approved equivalent Make. (ASS ROOM, MESH ROOM, SECUIRITY ROOM,EL UPS ROOM,CORRIDOR, STORE) | Nos. | 3347
5.1.4 | Supply, Installation, Testing & Commissioning of recessed mounted LED Downlighter, made of pressure die-cast Aluminium body with high quality diffuser. Luminaries should be with minimum system efficacy of 100Lumen/Watt and minimum system lumen output of 1600 maintained at 70% at the end of 50,000 burning hours. The luminaries should have CRI>80 and CCT of 6500K. Luminaries should withstand THD less than 10% and should have power factor > 0.90 . Driver efficiency should be 85%. Luminaries should comply with all the required IEC standards and should operate in a voltage range of 220 to 240 volts AC. Similar To Philips Green Perform LED Downlighter DN 394B LED 16S-6500 PSU WH or approved equivalent Make. | Nos. | 460
5.1.5 | Supply, Installation, Testing & Commissioning of LED Bulkhead Luminaries, made of high pressure die-cast Aluminium body with polycarbonate diffuser. Luminaries should be with minimum system efficacy of 60Lumen/Watt and minimum system lumen output of 600 maintained at 70% at the end of 50,000 burning hours. The luminaries should have CRI>80 and CCT of 6500K. Luminaries shall meet IP66 and IK09 protection with THD less than 20% and power factor > 0.90 . The total system power should not exceed 9 W including driver losses. Driver efficiency should be 85% . Luminaries should comply with all the required IEC standards and should operate in a voltage range of 220 to 240 volts AC. Similar To Philips Endura LED Bulkhead WT202W LED6S CW PSU S2 PC or approved equivalent Make. | Nos. | 883
5.1.6 | Supply, Installation, Testing & Commissioning of LED 2X2 recess mounting LED luminaries with soft opal diffuser provides high visual comfort enclosed in a polyester powder coated housing with high efficiency diffuser. It should be system lumen efficacy 100Lumen/Watt with system level luminous flux of 3400 lumens and system wattage of 34W, 50,000 hours burning life for the system at 70% lumen maintenance with a Color rendering index > 80 and Color temperature 6500K.PF > 0.9 and THD<10%. Luminaries must be sealed from bottom and has an inbuilt gear. The luminaries should be IP 20 protected. Luminaries should comply with all the required IEC standards and should operate in a voltage range of 220 to 240 volts AC. Similar to Philips Day line RC240B LED34S-6500 PSD OD WH or superior as per approved list. (Type-E, SCR, TOM, EFO) | Nos. | 1445
5.1.7 | Supply, Installation, Testing & Commissioning of surface mounted LED Luminaries, made up of CRCA sheet steel with toughened Glass diffuser. Luminaries should be with minimum system efficacy of 93Lumen/Watt and minimum system lumen output of 5600 maintained at 70% at the end of 50,000 burning hours. The luminaries should have CRI>80 and CCT of 6500K. Luminaries should withstand THD less than 10% and should have power factor > 0.90. The luminaries should be IP 65 protected. Luminaries should comply with all the required IEC standards and should operate in a voltage range of 220 to 240 volts AC. Similar To Philips Claria-CR652B LED56S or approved equivalent Make. (Ground level Under Concourse) | Nos. | 3398
5.1.8 | Supply, Installation, Testing & Commissioning of surface/Conduit LED Batten Luminaries, made up of CRCA sheet with glossy PC diffuser. Luminaries should be with minimum system efficacy of 105Lumen/Watt and minimum system lumen output of 2000 maintained at 70% at the end of 40,000 burning hours. The luminaries should have CRI>80 and CCT of 6500K. Luminaries should withstand THD less than 10% and should have power factor > 0.95 . Driver efficiency should be 85% . Luminaries should comply with all the required IEC standards and should operate in a voltage range of 140 to 270 volts AC. Similar To Philips Endura LED Batten BN108C LED 20S PSU CDL WH or approved equivalent Make. (EMERGENCY STAIRCASE) | Nos. | 393
5.1.9 | Supply, Installation, Testing & Commissioning of surface mounted LED Luminaries, made up of CRCA sheet steel with toughened Glass diffuser. Luminaries should be with minimum system efficacy of 92Lumen/Watt and minimum system lumen output of 3300 maintained at 70% at the end of 50,000 burning hours. The luminaries should have CRI>80 and CCT of 6500K. Luminaries should withstand THD less than 10% and should have power factor > 0.90. The luminaries should be IP 65 protected. Luminaries should comply with all the required IEC standards and should operate in a voltage range of 220 to 240 volts AC. Similar To Philips Claria-CR652B LED33S or approved equivalent Make. (Ground level Entry ) | Nos. | 841
5.1.10 | Supply, Installation, Testing & Commissioning of surface/Conduit LED Batten 2' Luminaries, made up of CRCA sheet with glossy PC diffuser. Luminaries should be with minimum system efficacy of 110Lumen/Watt and minimum system lumen output of 1150 maintained at 70% at the end of 40,000 burning hours. The luminaries should have CRI>80 and CCT of 6500K. Luminaries should withstand THD less than 10% and should have power factor > 0.95 . Driver efficiency should be 85% . Luminaries should comply with all the required IEC standards and should operate in a voltage range of 140 to 270 volts AC. Similar To Philips Smart Brite LED Batten BN021 LED 10S PSU or approved equivalent Make. (EMERGENCY STAIRCASE) | Nos. | 28
5.2 | Fans
5.2.1 | Supply, Installation, Testing and Commissioning of 230 V single phase, 1200 mm sweep ceiling fans with all standard accessories complete and suitable length down rod, duly painted, not exceeding minimum fan height of 2.4 m from floor as required. Fan shall be of Approved Make. | Nos. | 129
5.2.2 | Supply, Installation, Testing and Commissioning of 230 V single phase, 400 mm sweep, pedestal fans with inbuilt electronic regulators including all standard accessories as complete. Fan shall be of Approved Make. | Nos. | 48
5.4 | Poles
General Points
i) | Entry & exit pipes one for Power Cable and one for ELV cable. ELV cable pipe 35mm dia should go up to 2 meter.
ii) | Each Pole should have cable pullout hole of 15mm. At every 500mm starting from 4 meter up to 6 meter for monitoring other accessories. Pole switch should also have a terminal box of 75 mm. wide and 210mm. Long for accommodating ELV services connector etc.
iii) | Bajaj Cat. No. BOP-1030 / Philips / Keselec or equivalent welded base plate, pedestal of specified height to IS:2713 part II-1980 or latest as per specifications and drawings .
iv) | 1:3:6 concrete foundation and pedestal coping 300 dia of height as per specification and relevant IS and as required. Contractor to obtain approval of foundation design before proceeding further.
v) | 6 ways, 20A connector & 6A MCB mounted on 6mm thick painted MS/GI plate, insulated, and accommodated inside the pole with gasketed weather, vermin proof, hinged lockable covered GI/MS box or integral cast box in pedestal as required.
vi) | Wiring to Luminaries from the 2A, MCB, with 3 x 2.5 copper, stranded Conductor (P+N+PE) double sheathed wire and making connections & earthing of pole.
vii) | Painting of pole accessories with 2 coats of primer and 2 coats of oil paint of approved color.
viii) | Luminaries as specified with lamps, necessary cross arm to the luminaries, integral control gear and as under.
5.4.1 | 9.0 meter hot dipped galvanized Octagonal with single overhang arm & with foundation bolts, base plate complete with foundation, entry and exit pipes, control JB with connector generally as shown on drawings and as per specifications. | Nos. | 16
5.4.2 | 9.0 meter hot dipped galvanized Octagonal with double overhang arm & with foundation bolts, base plate complete with foundation, entry and exit pipes, control JB with connector generally as shown on drawings and as per specifications. | Nos. | 16
5.4.3 | 7.0 meter hot dipped galvanized Octagonal multi purpose pole with single overhang arm & with foundation bolts, base plate complete with foundation, entry and exit pipes, control JB with connector generally as shown on drawings and as per specifications. | Nos. | 288
5.4.4 | 7.0 meter hot dipped galvanized Octagonal multi purpose pole with double overhang arm & with foundation bolts, base plate complete with foundation, entry and exit pipes, control JB with connector generally as shown on drawings and as per specifications. | Nos. | 16
5.5 | Luminaries
5.5.1 | Supply, installation, testing and commissioning of 72 watts, 7200 Lumen output, street light luminaries with aesthetically designed die cast Aluminium housing POT optics reflector and toughened flat glass (IP 65). Similar to Philips Cat. No. BRP 410 LED or equivalent including Lamp. | Nos. | 591
5.5.2 | Supply, installation, testing & commissioning of twin dome aviation light of type BJAOL 2 with 2 nos. of 100 watts GLS lamp or equivalent LED type including lamps, mounting bracket, earthing, painting complete with accessories to automatically switch off lights. | Nos. | 32
5.6 | High Mast
5.6.1 | Supply, installation, Testing and Commissioning of 12 m high area lighting High Mast, suitable for 16 nos. 1X240 W LED luminaries complete with all standard accessories. The mast shall be in two section, hot dip galvanized and suitable for wind velocity as per IS 875. It shall also include accessories for high mast including head frame, steel wire rope 6 mm dia.(7/19 construction), trailing cable, double drum winch, galvanized lantern carriage arrangement suitable for 16 luminaires symmetrically and its control gear box and lightning finial and including the cost of providing supplying and fixing 16 nos. 1X240 W LED luminaires with die cast / extruded Aluminium body, pre anodized Aluminium asymmetric/symmetric reflector, IP 65 and above, heavy duty control gear housed in a weather proof housing equivalent to Philips cat no. BVP 410 LED 242 CW or equivalent. The price shall include others accessories like foundation bolts manufactured from special high tension steel along with nut, washer anchor plates, templates and control panel housing consisting of 63 A TPN MCB as incomer, digital timer contactor circuit for automatic control of luminaries as required with along with the following as required for complete functionality of the system. | Nos. | 16
a) | Earth station of Pipe earthing as per IEEE 80 -2000, and IS 3043 - 1987, including duplicate earth connection to the mast with 25X3 mm size GI flat.
b) | Suitable neon Twin dome Aviation lights as required.
c) | Suitable foundation for the Mast considering soil bearing capacity 10 Ton per Sqm, with base pedestal of approve design, incorporating a suitable cable looping box with terminal blocks MCB etc.
The mast shall have an external power tool installed inside the base compartment for its operation
Sub-total for A.05