## Light fixture
New Construction of GMERS Medical College Attached 650 Bedded Hospital Building ( Phase-II) at Vadnagar
Item No. | Item Description | Unit | Qty.
146 | Supplying and erecting LED indoor fittings with LEDs of wattage 0.2 Watt to 0.5 Watt assembled on single MCPCB, with housing used as a heat sink shall be made of thick sheet Steel conforming to IS: 513/CRCA polyester powder coated and high U.V. & corrosion resistance with diffuser and/or Polycarbonate optics with company mark/name 120 to 300 V,Power Factor more than 0.9, THD < 10 %, CCT 4000 K to 6500K, Uniformity ratio >0.7, Luminaire efficiency> 85 lumens/watt , LED driver efficiency > 85 % CREE / OSRAM / PHILIPS Lumileds / NICHIA / SEOUL/Bridgelux(U.S.A.) make LED used for luminaire. (Each fitting required LM-79 & LM-80 Certificates) (D) LED Panel Light with provision for Plane front frame with translucent cover fixed to housing complete. (f) upto 36 watts, 600 x 600 mm, Surge- 4KV Cat-lll with 5 (five) years of warrenty. | Nos. | 1750
147 | Supplying and erecting LED Clean room bottom opening screw less indoor fittings with IP 65, dust free & Zero Maintenance for hygenic facilities LEDs of wattage 0.2 Watt to 0.5 Watt assembled on single MCPCB, with housing used as a heat sink shall be made of thick sheet Steel conforming to IS: 513/CRCA polyester powder coated white afte rhosphochromate treatment and high U.V. & corrosion resistance with high quality polycarbonate opal diffuser for glare free uniform light distribution with company mark/name perating Voltage- 120 to 300 V, Operating temp.- -10 C to +45 C, Power Factor more than 0.9, THD < 10 %, CCT 4000 K to 6500K, System lumens - 3200, Uniformity ratio >0.7, Luminaire efficiency> 85 lumens/watt , LED driver efficiency > 85 % CREE / OSRAM / PHILIPS Lumileds / NICHIA / SEOUL/Bridgelux(U.S.A.) make LED used for luminaire. (Each fitting required LM-79 & LM-80 Certificates) (D) LED Panel Light with provision for Plane front frame with translucent cover fixed to housing complete. (f) upto 34 watts, 600 x 600 mm, Surge- 4KV Cat-lll with 5 (five) years of warrenty. | Nos. | 100
148 | Supplying and erecting 50 W LED Highbay Luminaire with IP 54 LEDs of wattage 0.2 Watt to 0.5 Watt assembled on single MCPCB, Body with PDC Material and high U.V. & corrosion resistance with high quality glass Transparent diffuser for glare free uniform light distribution with company mark/name perating Voltage- 160 to 270 V, Operating temp.- -10 C to +45 C, Power Factor more than 0.9, THD < 10 %, CCT 4000 K to 6500K, System lumens - 4500 Uniformity ratio >0.7, Luminaire efficiency> 85 lumens/watt , LED driver efficiency > 85 % CREE / OSRAM / PHILIPS Lumileds / NICHIA / SEOUL/Bridgelux(U.S.A.) make LED used for luminaire. (Each fitting required LM-79 & LM-80 Certificates) with 5 (five) years of warrenty. | Nos. | 60
149 | Supplying and erecting LED indoor fittings with LEDs of wattage 0.2 Watt to 0.5 Watt assembled on single MCPCB, with housing used as a heat sink shall be made of thick sheet Steel conforming to IS: 513/CRCA polyester powder coated and high U.V. & corrosion resistance with diffuser and/or Polycarbonate optics with company mark/name 120 to 300 V,Power Factor more than 0.9, THD < 10 %, CCT 4000 K to 6500K, Uniformity ratio >0.7, Luminaire efficiency> 85 lumens/watt , LED driver efficiency > 85 % CREE / OSRAM / PHILIPS Lumileds / NICHIA / SEOUL/Bridgelux(U.S.A.) make LED used for luminaire. (Each fitting required LM-79 & LM-80 Certificates) (C) Square/ Circular Surface/Recessed Mounted Downlight with provision for spring loaded mounting clips complete. (b) 10-15 watts, Surge-4 KV Cat-lll with 5 (five) years of warrenty. | Nos. | 2900
150 | Supplying and erecting LED indoor fittings with LEDs of wattage 0.2 Watt to 0.5 Watt assembled on single MCPCB, with housing used as a heat sink shall be made of thick sheet Steel conforming to IS: 513/CRCA polyester powder coated and high U.V. & corrosion resistance with diffuser and/or Polycarbonate optics with company mark/name 120 to 300 V,Power Factor more than 0.9, THD < 10 %, CCT 4000 K to 6500K, Uniformity ratio >0.7, Luminaire efficiency> 85 lumens/watt, LED driver efficiency > 85 % CREE / OSRAM / PHILIPS Lumileds / NICHIA / SEOUL/Bridgelux(U.S.A.) make LED used for luminaire. (Each fitting required LM-79 & LM-80 Certificates) (A) Tube Light with integral/ non-integral driver (c) 20-22 Watts, Surge - 4KV,IP-20 Cat-lll with 5 (five) years of warrenty. | Each | 700
151 | Supplying and erecting LED street light / Flood light fittings with High power White LEDs wattage of 1Watt and above assembled on single MCPCB, efficiency more than 130 lm/w and corrosion free High pressure die cast aluminum housing with smooth finish powder coated and heat sink extruded aluminium with diffuser and Polycarbonate optics/ lenses with company mark/name engraved or embossed 120 to 300 V,Power Factor more than 0.95, THD < 10 %, CCT 5000 K to 5700K, Uniformity ratio >0.45, Luminaire efficiency> 85 lumens/watt . LED driver efficiency > 85 %. CREE / OSRAM / PHILIPS Lumileds / NICHIA / SEOUL/ BridgeLux (U.S.A.) make LED used for luminaire. ( Each fittings required LM-79 & LM-80 certificates) (B) Flood Light (IP-65), Surge -4KV (e) above 150 to 240 watts Cat-lll with 5 (five) years of warrenty. | Each | 50
152 | Supplying and erecting LED street light / Flood light fittings with High power White LEDs wattage of 1Watt and above assembled on single MCPCB, efficiency more than 130 lm/w and corrosion free High pressure die cast aluminum housing with smooth finish powder coated and heat sink extruded aluminium with diffuser and Polycarbonate optics/ lenses with company mark/name engraved or embossed 120 to 300 V,Power Factor more than 0.95, THD < 10 %, CCT 5000 K to 5700K, Uniformity ratio >0.45, Luminaire efficiency> 85 lumens/watt . LED driver efficiency > 85 %. CREE / OSRAM / PHILIPS Lumileds / NICHIA / SEOUL/ BridgeLux (U.S.A.) make LED used for luminaire. ( Each fittings required LM-79 & LM-80 certificates) (B) Flood Light (IP-65), Surge -4KV (e) above 70 to 90 watts Cat-lll with 5 (five) years of warrenty. | Each | 50