LED LIGHT FITTINGS

1.0  The scope of work includes design, development, manufacturing, testing, supply, installation and commissioning of energy efficient luminaries complete with all accessories, LED lamps with suitable current control driver circuit including mounting arrangement for recessed type fittings, power distribution panel etc. The luminaries shall be suitable for rugged service under the operational and environmental conditions encountered during service. All the luminaries shall be supplied with associated driver circuit compatible with LEDs in all respect as required.

2.0  Illumination of minimum 7.0 Lux must be maintained on either side of the perimeter up to a distance of 20m all along; the pole design for mounting of CCTV camera shall also be used for mounting of LED lights of appropriate wattage capacity to ascertain the desired lux level throughout along the perimeter. The LED lights to be provided at 8m height at the end of cantilever.

3.0 Technical requirements of LED light fittings:

c. Technical requirements for LED

s) LED efficacy shall be greater than 110/180 Lumens/Watt @ 350mA drive current. In respect of LEDs of higher power ratings, drive current greater than 350mA can be accepted if the LED's LM 80 / IS: 16105 test reports support the same.

t) LED used should be of SMD type only.

u) LM-80/ IS: 16105 Test Reports of specific LED at the soldering point temperature of 85°C for the driving current at which the LEDs shall be driven, shall be obtained during procurement.

v) Reported life Span of LEDs used in the Luminare shall be greater than 50,000 Hrs at the soldering point temperature of 85°C and at the luminare driving current.

w) The LEDs shall comply to Photo biological Safety norms as per IEC 62471 / EN 62471/ IS: 16108.

x) View angle: Typical 60 deg /120 deg meeting the illumination requirements on either side of the perimeter.

y) Color temperature of the proposed white color LED shall be 5700K (i.e. 5665K±355K, as per ANSI standard C78.377A), Color point should fall within the 7 Step McAdam as per ANSI standard C78.377A.

z) Color Rendering Index (CRI) of minimum 80 (+5%) with cool white light output.

d. Technical requirements for LED driver

aa) The driver shall be of constant voltage and constant current type with internal surge protection device.

bb) Min. efficiency of driver: 90%.

cc) Power factor of complete fitting: Greater than 0.90

dd) The luminare should be operable with auto adjustable 140-270V input supply voltage using the same driver.

ee) In - built high and low voltage cut - offs : 140V (Low) and 270V (High)

ff) Short circuit protection /Over load protection

gg) Driver Surge Protection standard: Min 4kV. If a site/ location is prone to lightning and surges, 10 kV surge protection (external to the driver circuit) to be provided with the luminaire. The Surge Protection Device (SPD) should fail safe (i.e. without leading to fire hazard) and its failed status should be clearly visible through a flag/ indication.

hh) Total Harmonic Distortion (THD): Less than 20 % at full load

ii) Tc (Maximum Driver case temperature) must be declared for the luminaire.

jj) Isolated driver should be used.

kk) Potting of LED Driver: For driver power output rating < 50W, potted driver shall be preferable (but not mandatory). But for driver power output rating > 50W, potted driver shall be a mandatory requirement.

ll) The power supply shall be connected to the LED PCBs through proper connectors.

mm) EMI/ EMC compliance: Compliance to the following EMI/ EMC standards:

i. CISPR15/IS:6573

ii. IEC: 61547 (reference standards are listed as follows)

- IEC 61000 – 4 - 2/ IS:14700 P art 3: Sec 2

- IEC 61000 – 4 - 3

- IEC 61000 - 4 - 4/ IS: 14700 Part 3: Sec 4

- IEC 61000 - 4 – 5 3 kV (or 4 kV if so offered by the contractor)

- IEC 61000 – 4 - 6

- IEC 61000 – 4 -11/ IS: 14700 Part 3: Sec 11

iii. IEC: 61000 - 3 - 2 (Class C)/ IS: 1534 Part 1 (d) IEC: 61 000 - 3 - 3 / IS 14700: Part 3: Sec 2

nn) Driver shall comply with the safely requirements laid down in IEC: 61347 - 2 - 13/ EN: 61347-2-13/IS: 15885-2-13.

oo) Driver shall also comply with the performance requirements as per IEC: 62384/ IS: 16104.

e. Technical requirements of electronic components used

The circuit boards and electronic components to be used in the luminaries should be of suitable rating/ type so as to provide reliable functioning. Following document needs to be furnished:

Junction temperature rating of I. C. shall be obtained for the luminare.

Capacitor type and temperature rating shall be obtained for the luminare.

Material of resister shall be furnished

Junction / channel temperature rating of switching device s like MOSFET and transistor shall be obtained.

MCPCB is to be used for mounting of LBDs.

FR4 grade PCBs of min. thickness of 1.6 mm shall be used in driver circuits.

f. Technical requirements of Luminaries:

The luminare should throw the perfect amount of uniform light with exactly the desired intensity at a given spacing as mentioned in the tender document along with better light control. The bidder should submit the certified photometric report as per IESNA LM-79/ IS: 16106, from a NABL accredited laboratory to validate the photometric claims.

Minimum 40 nos. of LED lamps shall be used in each luminare.

The min. system lumen efficacy of the Luminare shall be 110/ 180 lumens/Watt.

The Luminare must have secondary lens/ optics. Though the secondary lens/ optics do result in minor loss of lumens, it is nevertheless a must to distribute the light output of the LEDs so as to achieve the desired polar curve characteristics for the Luminare — no exemption shall be permitted on this account. The material of lens should preferably be PMMA.

Housing of luminaire: Pressure die - cast LM6/ADC12/LM24 housing

Cover type: Heat Resistant Toughened glass of minimum 4 mm thick or UV stabilized polycarbonate cover.

Adequate heat sink with proper thermal management shall be provided.

The fixture should be able to work properly with humidity range of 10%-95% RH.

The fixture should have corrosion resistance polyester powder coating.

Housing protection: Minimum IP - 65. If the LEDs and LED Driver are in different compartments, then the two compartments must be individually IP – 65 or better.

Impact Resistance: IK - 08

Temperature rise test: When the luminare has stabilized thermally, soldering point temperature of the LEDs must be equal to or less than 85°C. Temperature rise (above ambient) of heat sink should generally remain within 20°C -relaxation on this account can be granted as long as the soldering point temperature limit of 85°C is not violated and there is no unacceptable out come.

During procurement, the photometric data report in respect of the luminare offered (through DTA Lux, CALCULUX or other simulation software) should be obtained. IES Photometric File is also to be supplied and firms to be warned of serious consequences against submission of a tampered/ doctored report.