## Sheet1
LIGHTING (ILLUMINATION) BOQ
SL.NO | TYPE OF LIGHT FITTING | UNIT | QTY | REMARKS
1 | TYPE A. 203W HIGH BAY WIDE BEAM LED FITTING IP65, CCT 4000 TO 5700 DEGREE KELVIN, CRI ≥80, UGR <22 LPW ≥100 & IK 08 FIXED WITH DOWN RODS AND BALL/ SOCKET FITTING. SIMILAR TO DISANO ASTRO 2786 330166-07. | NOS. | 1104
2 | Type-B. 36/40W RECESS MOUNTED LED PANEL 3960 LUMEN IP40 CCT 5700 DEGREE KELVIN CRI ≥80 UGR <19 LPW ≥100 & IK 06. | NOS. | 400
3 | Type-C. 36/40W RECESS MOUNTED LED PANEL 3960 LUMEN IP40 CCT 5700 DEGREE KELVIN CRI ≥80 UGR <19 LPW ≥100 & IK 06. WITH EMERGENCY KIT FOR 3 HOURS BACK UP AND BLF SHOULD BE BETWEEN 17 TO 20%. | NOS. | 178
4 | Type D.36/40W SURFACE MOUNTED LED PANEL 3960 LUMEN IP40 CCT 5700 DEGREE KELVIN CRI ≥80 UGR <19 LPW ≥100 & IK 06. | NOS. | 27
5 | Type E.36/40W SURFACE MOUNTED LED PANEL 3960 LUMEN IP40 CCT 5700 DEGREE KELVIN CRI ≥80 UGR <19 LPW ≥100 & IK 06. WITH EMERGENCY KIT FOR 3 HOURS BACK UP AND BLF SHOULD BE BETWEEN 17 TO 20%. | NOS. | 18
6 | Type F, 21W RECESSED LED DOWN LIGHT FITTING IP44 RATING. CCT 5700 DEGREE KELVIN CRI ≥90 UGR <22 LPW ≥100 & IK 04.SIMILAR TO DISANO 884 COMPACT 156425-00. . | NOS. | 219
7 | Type G, 21W RECESSED LED DOWN LIGHT FITTING IP44 RATING. CCT 5700 DEGREE KELVIN CRI ≥90 UGR <22 LPW ≥100 & IK 04.SIMILAR TO DISANO 884 COMPACT 156425-00. WITH EMERGENCY KIT FOR 3 HOURS BACK UP AND BLF SHOULD BE BETWEEN 17 TO 20%. | NOS. | 34
8 | Type H. 12W LED MIRROR LIGHT 1000 LUMEN,IP44 RATING & CCT 5700 DEGREE KELVIN CRI ≥80 UGR <22 LPW ≥100 & IK 08. | NOS. | 221
9 | Type I.15W RECESSED LED DOWN LIGHT FITTING IP44 RATING. CCT 5700 DEGREE KELVIN CRI ≥90 UGR <22 LPW ≥100 & IK 07.SIMILAR TO DISANO 883 COMPACT 156415-00. WITH EMERGENCY KIT FOR 3 HOURS BACK UP AND BLF SHOULD BE BETWEEN 17 TO 20%. | NOS. | 232
10 | Type J. 21W SURFACE MOUNTED LED DOWN LIGHT FITTING IP40 RATING. CCT 5700 DEGREE KELVIN CRI ≥80 UGR <22 LPW ≥60 & IK 04.SIMILAR TO DISANO 781 COMPACT 156301-00. WITH EMERGENCY KIT FOR 3 HOURS BACK UP AND BLF SHOULD BE BETWEEN 17 TO 20%. | NOS. | 12
11 | Type K. 15W SURFACE MOUNTED LED DOWN LIGHT FITTING IP44 RATING. CCT 5700 DEGREE KELVIN CRI ≥90 UGR <22 LPW ≥100 & IK 04.SIMILAR TO DISANO 884 COMPACT 156425-00. | NOS. | 32
12 | Type L. 15W SURFACE MOUNTED LED DOWN LIGHT FITTING IP44 RATING. CCT 5700 DEGREE KELVIN CRI ≥90 UGR <22 LPW ≥100 & IK 04.SIMILAR TO DISANO 884 COMPACT 156425-00. WITH EMERGENCY KIT FOR 3 HOURS BACK UP AND BLF SHOULD BE BETWEEN 17 TO 20%. | NOS. | 0
13 | Type M. 25W RECESSED LED DOWN LIGHT FITTING IP44 RATING. CCT 5700 DEGREE KELVIN CRI ≥90 UGR <22 LPW ≥100 & IK 04.SIMILAR TO DISANO 884 COMPACT 156425-00. | NOS. | 18
14 | Type N. 25W RECESSED LED DOWN LIGHT FITTING IP44 RATING. CCT 5700 DEGREE KELVIN CRI ≥90 UGR <22 LPW ≥100 & IK 04.SIMILAR TO DISANO 884 COMPACT 156425-00. WITH EMERGENCY KIT FOR 3 HOURS BACK UP AND BLF SHOULD BE BETWEEN 17 TO 20%. | NOS. | 0
15 | Type O. 135W HIGH BAY WIDE BEAM LED FITTING IP65, CCT 4000 TO 5700 DEGREE KELVIN, CRI ≥80, UGR <22 LPW ≥100 & IK 08 FIXED WITH DOWN RODS AND BALL/ SOCKET FITTING. SIMILAR TO DISANO ASTRO 2786 330165-07. | NOS. | 127
16 | Type P. 101W HIGH BAY WIDE BEAM LED FITTING IP65, CCT 4000 TO 5700 DEGREE KELVIN, CRI ≥80, UGR <22 LPW ≥100 & IK 08 FIXED WITH DOWN RODS AND BALL/ SOCKET FITTING. SIMILAR TO DISANO ASTRO 2786 330164-07. | NOS. | 90
17 | Type Q. 34W SURFACE MOUNTED TYPE LED WITH OPAL DIFFUSER IP65 5585LMEN CCT4000 TO 6000 DEGREE KELVINCRI ≥80 UGR <22 LPW ≥100 & IK 08. SIMILAR TO DISANO 963 HYDRO+6 164764-00. | NOS. | 58
18 | Type R. 34W SURFACE MOUNTED TYPE LED WITH OPAL DIFFUSER IP65 5585 LUMEN CCT4000 TO 6000 DEGREE KELVIN CRI ≥80 UGR <22 LPW ≥100 & IK 08. SIMILAR TO DISANO 963 HYDRO+6 164764-07. WITH EMERGENCY KIT FOR 3 HOURS BACK UP AND BLF SHOULD BE BETWEEN 17 TO 20% | NOS. | 12
19 | Type S, 29W SURFACE MOUNTED 120W LED LIGHT ATEX- ZONE2 Exde T4 EXPLOSION PROOF TYPE.SIMILAR TO STAHL / COOPER / CIAG / CORTEAM / BEGHELLI. | NOS. | 3
20 | TYPE T. 50W SURFACE MOUNTED TYPE LED WITH OPAL DIFFUSER IP65 5585LMEN CCT4000 TO 6000 DEGREE KELVIN CRI ≥80 UGR <22 LPW ≥100 & IK 08. SIMILAR TO DISANO 962 HYDRO 164761-00. | NOS. | 64
21 | TYPE U. 50W SURFACE MOUNTED TYPE LED WITH OPAL DIFFUSER IP65 5585LMEN CCT4000 TO 6000 DEGREE KELVIN CRI ≥80 UGR <22 LPW ≥100 & IK 08. SIMILAR TO DISANO 962 HYDRO 164761-07.WITH EMERGENCY KIT FOR 3 HOURS BACK UP AND BLF SHOULD BE BETWEEN 17 TO 20%. | NOS. | 30
22 | TYPE V. 138W ASYMMETRIC BEAM LED FITTING IP65, CCT 4000 TO 5700 DEGREE KELVIN, CRI ≥80, LPW ≥100 & IK 08 . SIMILAR TO DISANO 1898 RODIO 414922-00. | NOS. | 40
23 | TYPE W. 196W ASYMMETRIC BEAM LED FITTING IP65, CCT 4000 TO 5700 DEGREE KELVIN, CRI ≥80, LPW ≥100 & IK 08. SIMILAR TO DISANO 1898 RODIO 414923-00. | NOS. | 73
24 | TYPE X. 119W LED STREET LIGHT FITTING WITH FLAT GLASS IP65 RATING MOUNTED ON 8M HEIGHT POLE. CCT 4000 TO 5700 DEGREE KELVIN, CRI ≥80, LPW ≥100 & IK 09. SIMILAR TO DISANO 3284 ROLLE 330442-00. THE COST TO INCLUDE THE SUPPLY AND INSTALLATION OF LED STREET LIGHT & 8MTR CONICAL POLE ALONG WITH RELATED CIVIL WORKS. | NOS. | 67
25 | TYPE Y. 79W ASYMMETRIC BEAM LED FITTING IP65, CCT 4000 TO 5700 DEGREE KELVIN, CRI ≥80, LPW ≥100 & IK 08. SIMILAR TO DISANO 1898 RODIO 414920-00. | NOS. | 51
26 | Type Z. 35W ASYMMETRIC BEAM LED FITTING IP65, CCT 4000 TO 5700 DEGREE KELVIN, CRI ≥80, LPW ≥90 & IK 08 . SIMILAR TO DISANO 1711 CRIPTO 413010-00. | NOS. | 67
27 | TYPE A1. 60W HIGH BAY WIDE BEAM LED FITTING IP65, CCT 6500 DEGREE KELVIN, CRI ≥80, UGR <22 LPW ≥100 & IK 08 FIXED WITH DOWN RODS AND BALL/ SOCKET FITTING. SIMILAR TO 48 Z - VALUE HIGHBAY LED 60W 6500K 60W High Bay Light | NOS. | 9
28 | TYPE B1. 29W RECESSED LED DOWN LIGHT FITTING IP44 RATING. CCT 5700 DEGREE KELVIN CRI ≥90 UGR <19 LPW ≥100 & IK 07.SIMILAR TO DISANO 884 COMPACT 156427-00 | NOS. | 2
29 | TYPE C1. 10W DOWN LIGHT ( 21- TIME OFFICE, CANTEEN & CHANGING ROOM) IN PANTRY | NOS. | 20
30 | TYPE D1. 15W SURFACE MOUNTED LIGHT FIXTURE | NOS. | 2