## BoQ1
4.00 | S & F in replacement existing unsv batten type fitting 4 feet long suitable for LED tube 20W LED including LED tube 4 feet long of 20W having bipin holder, connector block etc complete all accessories prewired and connecting electrically to ceiling rose using PVC insulated and overall sheathed flexible copper conductor cable of size 0.75 sqmm 3 core all as required at site or directed. Note : (i) Driver efficiency more than 85% ( Constant current driver) (ii) Non isolated type driver (iii) THD less than 20% (iv) LED driver current less than 60 mA (v) Efficiency of LED Chip more than 130 lm/watt (vi) Efficiency of LED Fixture 100 lm/watt (vii) Surge protection 2.5 KV & above as per IEC standard (viii) working humidity 95%RH (ix) LED Make Nichia /Philips lumiled/ Cree/Osram/Seoul/Bridgelux/Nationsear (x) Life 50000 Hrs at 70% lumes (xi) CRI more than 80 (xii) Working temp -10 degree to 50 degree C (xiii) Heat Sink extruded aluminum (xiv) junction temperature 85 degree C (xv) Body of fitting Extruded Aluminum (xvi) impact code Min IK 03 or more ( xvii) LM79 report from thir party (instead of company in house lab) NABL/UL accredited lab (xviii) LM 80 report from LED manufacturer (xix) Low/High voltage, reverse polarity, overload and short circuit protection inbuilt in fixture (xx) IP-20 .(xxi) Test certificates to be submitted before commencement of work/ claiming for payment .(xxii) Warranty certificate for minimum 2 years to be submitted from OEM. | 1150.00 | Each
5.00 | Supply and fixing in replacement bulk head light fitting LED 1X10watts suitable lamp complete connecting electricaly to ceiling rose using cord flexible 3 core PVC insulated over all sheathed with flexible copper conductor of size 0.75 sqmm all as required. Note : (i) Driver efficiency more than 85% ( Constant current driver) (ii) Non isolated type driver (iii) THD less than 20% (iv) LED driver current less than 60 mA (v) Efficiency of LED Chip more than 130 lm/watt (vi) Efficiency of LED Fixture 100 lm/watt (vii) Surge protection 2.5 KV & above as per IEC standard (viii) working humidity 95%RH (ix) LED Make Nichia /Philips lumiled/ Cree/Osram/Seoul/Bridgelux/Nationsear (x) Life 50000 Hrs at 70% lumes (xi) CRI more than 80 (xii) Working temp -10 degree to 50 degree C (xiii) Heat Sink extruded aluminum (xiv) junction temperature 85 degree C (xv) Body of fitting Extruded Aluminum (xvi) impact code Min IK 03 or more ( xvii) LM79 report from thir party (instead of company in house lab) NABL/UL accredited lab (xviii) LM 80 report from LED manufacturer (xix) Low/High voltage, reverse polarity, overload and short circuit protection inbuilt in fixture (xx) IP-20 .(xxi) Test certificates to be submitted before commencement of work/ claiming for payment .(xxii) Warranty certificate for minimum 2 years to be submitted from OEM. | 220.00 | Each
6.00 | Supply and fix in replacement existing UNSV Recess/suspended slim LED panel light with powder coated rim 36 watt of size 2x2 feet high efficiency designer recessed mirror optic luminary with ceiling cut out size 36 watt including LED lamps complete including connecting electricaly to ceiling rose using cord flexible 3 core PVC insulated over all sheathed with flexible copper conductor of size 0.75 sqmm all as required and specified by Engr-in-Charge. Note : (i) Driver efficiency more than 85% ( Constant current driver) (ii) Non isolated type driver (iii) THD less than 20% (iv) LED driver current less than 60 mA (v) Efficiency of LED Chip more than 130 lm/watt (vi) Efficiency of LED Fixture 100 lm/watt (vii) Surge protection 2.5 KV & above as per IEC standard (viii) working humidity 95%RH (ix) LED Make Nichia /Philips lumiled/ Cree/Osram/Seoul/Bridgelux/Nationsear (x) Life 50000 Hrs at 70% lumes (xi) CRI more than 80 (xii) Working temp -10 degree to 50 degree C (xiii) Heat Sink extruded aluminum (xiv) junction temperature 85 degree C (xv) Body of fitting Extruded Aluminum (xvi) impact code Min IK 03 or more ( xvii) LM79 report from thir party (instead of company in house lab) NABL/UL accredited lab (xviii) LM 80 report from LED manufacturer (xix) Low/High voltage, reverse polarity, overload and short circuit protection inbuilt in fixture (xx) IP-20 .(xxi) Test certificates to be submitted before commencement of work/ claiming for payment .(xxii) Warranty certificate for minimum 2 years to be submitted from OEM. | 35.00 | Each
7.00 | S&F in replacement existing UNSV decorative round surface mounted slim LED panel of 18 watt with powder coated finished in white housing complete with all accessories and including LED lamp, connection up with three core twisted flexibe copper conductor cable with suitable size. Note : (i) Driver efficiency more than 85% ( Constant current driver) (ii) Non isolated type driver (iii) THD less than 20% (iv) LED driver current less than 60 mA (v) Efficiency of LED Chip more than 130 lm/watt (vi) Efficiency of LED Fixture 100 lm/watt (vii) Surge protection 2.5 KV & above as per IEC standard (viii) working humidity 95%RH (ix) LED Make Nichia /Philips lumiled/ Cree/Osram/Seoul/Bridgelux/Nationsear (x) Life 50000 Hrs at 70% lumes (xi) CRI more than 80 (xii) Working temp -10 degree to 50 degree C (xiii) Heat Sink extruded aluminum (xiv) junction temperature 85 degree C (xv) Body of fitting Extruded Aluminum (xvi) impact code Min IK 03 or more ( xvii) LM79 report from thir party (instead of company in house lab) NABL/UL accredited lab (xviii) LM 80 report from LED manufacturer (xix) Low/High voltage, reverse polarity, overload and short circuit protection inbuilt in fixture (xx) IP-20 .(xxi) Test certificates to be submitted before commencement of work/ claiming for payment .(xxii) Warranty certificate for minimum 2 years to be submitted from OEM. | 35.00 | Each
8.00 | S&F in replacement existing UNSV decorative square recess mounted slim LED panel of 18 watt with powder coated finished in white housing complete with all accessories and including LED lamp, connection up with three core twisted flexibe copper conductor cable with suitable size. Note : (i) Driver efficiency more than 85% ( Constant current driver) (ii) Non isolated type driver (iii) THD less than 20% (iv) LED driver current less than 60 mA (v) Efficiency of LED Chip more than 130 lm/watt (vi) Efficiency of LED Fixture 100 lm/watt (vii) Surge protection 2.5 KV & above as per IEC standard (viii) working humidity 95%RH (ix) LED Make Nichia /Philips lumiled/ Cree/Osram/Seoul/Bridgelux/Nationsear (x) Life 50000 Hrs at 70% lumes (xi) CRI more than 80 (xii) Working temp -10 degree to 50 degree C (xiii) Heat Sink extruded aluminum (xiv) junction temperature 85 degree C (xv) Body of fitting Extruded Aluminum (xvi) impact code Min IK 03 or more ( xvii) LM79 report from thir party (instead of company in house lab) NABL/UL accredited lab (xviii) LM 80 report from LED manufacturer (xix) Low/High voltage, reverse polarity, overload and short circuit protection inbuilt in fixture (xx) IP-20 .(xxi) Test certificates to be submitted before commencement of work/ claiming for payment .(xxii) Warranty certificate for minimum 2 years to be submitted from OEM. | 30.00 | Each
9.00 | M & L for replacement of existing old u/s mirror light fittings with sleek energy efficient decorative LED mirror light 10 watts, 2 feet with diffuser complete with all accessories prewired and making connection with 3 core copper flexible cable of size 0.75 Sqmm from ceilling rose/PVC connector to light fittings ( fittings shall be fitted on two plastic square/round block. Note : (i) Driver efficiency more than 85% ( Constant current driver) (ii) Non isolated type driver (iii) THD less than 20% (iv) LED driver current less than 60 mA (v) Efficiency of LED Chip more than 130 lm/watt (vi) Efficiency of LED Fixture 100 lm/watt (vii) Surge protection 2.5 KV & above as per IEC standard (viii) working humidity 95%RH (ix) LED Make Nichia /Philips lumiled/ Cree/Osram/Seoul/Bridgelux/Nationsear (x) Life 50000 Hrs at 70% lumes (xi) CRI more than 80 (xii) Working temp -10 degree to 50 degree C (xiii) Heat Sink extruded aluminum (xiv) junction temperature 85 degree C (xv) Body of fitting Extruded Aluminum (xvi) impact code Min IK 03 or more ( xvii) LM79 report from thir party (instead of company in house lab) NABL/UL accredited lab (xviii) LM 80 report from LED manufacturer (xix) Low/High voltage, reverse polarity, overload and short circuit protection inbuilt in fixture (xx) IP-20 .(xxi) Test certificates to be submitted before commencement of work/ claiming for payment .(xxii) Warranty certificate for minimum 2 years to be submitted from OEM. | 200.00 | Each
10.00 | S & F in replacement existing unsv CFL lamp with LED 7 watt PF>0.90, 230 volts retrofit type complete all as specified and directed. Note : (i) Driver efficiency more than 85% ( Constant current driver) (ii) Non isolated type driver (iii) THD less than 20% (iv) LED driver current less than 60 mA (v) Efficiency of LED Chip more than 130 lm/watt (vi) Efficiency of LED Fixture 100 lm/watt (vii) Surge protection 2.5 KV & above as per IEC standard (viii) working humidity 95%RH (ix) LED Make Nichia /Philips lumiled/ Cree/Osram/Seoul/Bridgelux/Nationsear (x) Life 50000 Hrs at 70% lumes (xi) CRI more than 80 (xii) Working temp -10 degree to 50 degree C (xiii) Heat Sink extruded aluminum (xiv) junction temperature 85 degree C (xv) Body of fitting Extruded Aluminum (xvi) impact code Min IK 03 or more ( xvii) LM79 report from thir party (instead of company in house lab) NABL/UL accredited lab (xviii) LM 80 report from LED manufacturer (xix) Low/High voltage, reverse polarity, overload and short circuit protection inbuilt in fixture (xx) IP-20 .(xxi) Test certificates to be submitted before commencement of work/ claiming for payment .(xxii) Warranty certificate for minimum 2 years to be submitted from OEM. | 450.00 | Each
11.00 | S & F in replacement existing unsv CFL lamp with LED 9 watt PF>0.90, 230 volts retrofit type complete all as specified and directed. Note : (i) Driver efficiency more than 85% ( Constant current driver) (ii) Non isolated type driver (iii) THD less than 20% (iv) LED driver current less than 60 mA (v) Efficiency of LED Chip more than 130 lm/watt (vi) Efficiency of LED Fixture 100 lm/watt (vii) Surge protection 2.5 KV & above as per IEC standard (viii) working humidity 95%RH (ix) LED Make Nichia /Philips lumiled/ Cree/Osram/Seoul/Bridgelux/Nationsear (x) Life 50000 Hrs at 70% lumes (xi) CRI more than 80 (xii) Working temp -10 degree to 50 degree C (xiii) Heat Sink extruded aluminum (xiv) junction temperature 85 degree C (xv) Body of fitting Extruded Aluminum (xvi) impact code Min IK 03 or more ( xvii) LM79 report from thir party (instead of company in house lab) NABL/UL accredited lab (xviii) LM 80 report from LED manufacturer (xix) Low/High voltage, reverse polarity, overload and short circuit protection inbuilt in fixture (xx) IP-20 .(xxi) Test certificates to be submitted before commencement of work/ claiming for payment .(xxii) Warranty certificate for minimum 2 years to be submitted from OEM. | 450.00
12.00 | S & F in replacement existing unsv CFL lamp with LED 12 watt PF>0.90, 230 volts retrofit type complete all as specified and directed. Note : (i) Driver efficiency more than 85% ( Constant current driver) (ii) Non isolated type driver (iii) THD less than 20% (iv) LED driver current less than 60 mA (v) Efficiency of LED Chip more than 130 lm/watt (vi) Efficiency of LED Fixture 100 lm/watt (vii) Surge protection 2.5 KV & above as per IEC standard (viii) working humidity 95%RH (ix) LED Make Nichia /Philips lumiled/ Cree/Osram/Seoul/Bridgelux/Nationsear (x) Life 50000 Hrs at 70% lumes (xi) CRI more than 80 (xii) Working temp -10 degree to 50 degree C (xiii) Heat Sink extruded aluminum (xiv) junction temperature 85 degree C (xv) Body of fitting Extruded Aluminum (xvi) impact code Min IK 03 or more ( xvii) LM79 report from thir party (instead of company in house lab) NABL/UL accredited lab (xviii) LM 80 report from LED manufacturer (xix) Low/High voltage, reverse polarity, overload and short circuit protection inbuilt in fixture (xx) IP-20 .(xxi) Test certificates to be submitted before commencement of work/ claiming for payment .(xxii) Warranty certificate for minimum 2 years to be submitted from OEM. | 450.00 | Each
13.00 | S & F in replacement Bldg LED security light fittings on Bldg of height not exceeding 7.5 mtrs, comprising of epoxy powder coated housing, enclosed with glass cover in frame, for efficiency not less than 95 lumens/Watt, and minimum wattage capacity of 30 W with ingress protection IP 65/66 and external SPD of capacity 5 KV in addition to inbuilt with drive complete, including & fixed to 25 mm dia medium grade GI pipe bracket of length not less than 1.20 cm bend to 120 degree shape with necessary GI clamps 50mmx6mm MS strip bend to required shape, nut bolts etc and 1.5 Sqmm 3.5 core PVC flexible copper cable from junction box to fitting to be layed /drawn inside steel tubler pole complete and testing on completion all as specified and as directed. Note : (i) Driver Efficacy – more than 85% ( constrant current driver).(ii)Driver Type – Potted (iii) THD - < 10% (iv)Led Driver Current – less than 750 mA(v) Efficacy of Led Fixtrue – 100 lm/watt ( minimum) (vi) Efficacy of Led Chip – more than 130 lm/watt( Vii) Surge Protection – 4 KV & above as per IEC standard inbuilt in Driver and External SPD 5KV (vii) Working Humidity - 10% to 90% RH (ix) Led Make – Nichia/Philips Lumiled/ Cree /Osram/ Seoul (x) Life – 50,000 hours at 70% lumens(xi) CRI – more than 70 (xii) Lens – Each Led shall be of High Power ( 1 to 3 watt only) with mandatory modular lens. (xiii) Working Temp – 0 to 50 degree C. (xiv) Heat Sink – Pressure die cast aluminium (xv) Junciton Temp – 100 degree C (xvi) Body of Fitting – Pressue Die Cast with company logo / make engraved or embossed in housing LM 6 Grade.(xvii) Impact code – Min IK05 or more (xviii) LM79 report from Third Party ( instead of company in house lab) NABL /UL accredited lab. (xix) LM80 report from Led Manufacturer.(xx) Low/High voltage, reverse polarity, overload and short circuit protection inbuilt in fixtrue.(xxi) MS Clamp fittings with nut bolts and GI bracket, junction box included in the rate.(xxii) Test certificates to be submitted before commencement of work/ claiming for payment .(xxiii) Warranty certificate for minimum 2 years to be submitted from OEM. | 55.00 | Each
14.00 | S&F in replacement of UNSV security gate lights LED post top lantern type with IP 65 protection of wattage 40 W (luminous efficacy not less than 95 lumens/watt) complete all as directed and specified. Note : (i) Driver Efficacy – more than 85% ( constrant current driver).(ii)Driver Type – Potted (iii) THD - < 10% (iv)Led Driver Current – less than 750 mA(v) Efficacy of Led Fixtrue – 100 lm/watt ( minimum) (vi) Efficacy of Led Chip – more than 130 lm/watt( Vii) Surge Protection – 4 KV & above as per IEC standard inbuilt in Driver and External SPD 5KV (vii) Working Humidity - 10% to 90% RH (ix) Led Make – Nichia/Philips Lumiled/ Cree /Osram/ Seoul (x) Life – 50,000 hours at 70% lumens(xi) CRI – more than 70 (xii) Lens – Each Led shall be of High Power ( 1 to 3 watt only) with mandatory modular lens. (xiii) Working Temp – 0 to 50 degree C. (xiv) Heat Sink – Pressure die cast aluminium (xv) Junciton Temp – 100 degree C (xvi) Body of Fitting – Pressue Die Cast with company logo / make engraved or embossed in housing LM 6 Grade.(xvii) Impact code – Min IK05 or more (xviii) LM79 report from Third Party ( instead of company in house lab) NABL /UL accredited lab. (xix) LM80 report from Led Manufacturer.(xx) Low/High voltage, reverse polarity, overload and short circuit protection inbuilt in fixtrue.(xxi) MS Clamp fittings with nut bolts and GI bracket, junction box included in the rate.(xxii) Test certificates to be submitted before commencement of work/ claiming for payment .(xxiii) Warranty certificate for minimum 2 years to be submitted from OEM. | 12.00 | Each
15.00 | Sch of Credit = 36735.00
16.00 | Note: In case the tenderer quotes different rates for similar item then lowest rate shall only be applicable for payment and contractor shall not have any claim on this account.