## Sheet1
Sr. No. | Discription | Unit | Quantity | Rate/Unit | Amount
1 | Supply of following rating high efficacy and low power consumption LED Light, cover/ diffuser should be made of virgin non- yellowing PC (Poly Carbonate) and should have minimum 100 Lumens/ watt, suitable mounting arrangements, IP 20 or higher, CRI minimum 80, the total power consumption should not more than 110% of ratedcapacity of LED light, an operating voltage range of 140-270 V, power factor ≥0.95, THD <10%, complete as per technical specification.
1.01 | Recessed indoor type, round in shape, Backlit Downlight with pressure die-cast aluminium heat sink/Housing & the minimum system Lumen output of 2000 lumens and maximum system wattage should not increased 20 (± 10%) Watt, suitable for replacement (in terms of size) of existing Philips make, cat no. FBH 145/218 fittings] etc. complete as per technical specification. | Each | 370
1.02 | Recessed indoor type, square in shape, Backlit Downlight with CRCA heat sink/Housing & the minimum system Lumen output of 2000 lumens and maximum system wattage should not increased 20 (± 10%) Watt, suitable for replacement (in terms of size) of existing Philips make, cat no. FBS 285/218 fittings] etc. complete as per technical specification. | Each | 120
1.03 | Recessed indoor type, square in shape (2'x2'), Backlit Downlight with CRCA heat sink/Housing & the minimum system Lumen output of 3600 lumens and maximum system wattage should not increased 36 (±10%) Watt, Unified Glare Rating (UGR) should be ≤ 19, suitable for replacement (in terms of size) of existing Philips make, cat no. Wing C fittings etc. complete as per technical specification. | Each | 490
1.04 | Retrofit type, 4' long Aluminium extrusion polycarbonate T8 tube rod complete with batten, minimum system lumen output shall be 2000 Lumens and maximum system wattage of 20 Watt (± 10%), etc complete as per technical specification. | Each | 500
2 | Supply of LED flood light fitting having minimum Lumens system output of 11000 Lumens and maximum system wattage of 100 (± 10%) Watt and housing should be high pressure die cast aluminum/ standard alloy for out door application with toughened glass, luminairies Efficiency minimum 110 Lumens per watt, IP 65 or higher, CRI minimum 70 and suitable for operating voltage range of 140-270 V, IK rating 07 or above, power factor ≥0.95, THD <10%, surge protection 4 KV or higher, etc. complete as per techinal specification. | Each | 50
3 | Driver for 18 watt LED fitting round in shape as per item no. 1.01 | nos. | 40
4 | Driver for 18 watt LED Fitting Square in shape as per item no. 1.02 | nos. | 15
5 | Driver for 36 watt (2’x2’) fitting as per item no. 1.03. | nos. | 50
6 | Tube 18/20 watt (4’) fitting as per item no. 1.04. | nos. | 50
7 | Driver for 100 watt flood fitting as per item no. 2. | nos. | 5
Total Rs.