S&F in replacement of conventional street light fitting any type/capacity with LED street light fitting 45W (IP-66) with integrated lens for asymmetrical light distribution, system lumen output of ≥ 4600 (± 2.5%) lumens, system efficacy ≥ 100 lm/W, LED lumen efficacy ≥ 120 lm/W, CCT 3000K~6500K, CRI >70, electronic driver, 10 kV in-built surge protection, Output open/short circuit protection, phase to phase protection, over-voltage protection, etc. as per IS-15885, THD<10%, PF ≥ 0.95, housed in pressure die cast aluminium housing including necessary fabrication for fixing of LED stree tlight in existing GI bracket i.e GI reducer all as per directed by Engineer-in-Charge. Havells Cat No. ENDURAPEARLNEOSL45WLED757SASYTOPC or equivalent as mentioned in the APPENDIX 'B' .

Qty : 346 No’s.

S&F in replacement of conventional street light fitting any type/capacity with LED street light fitting 60W (IP-66) with integrated lens for asymmetrical light distribution, system lumen output of ≥ 6500 (± 2.5% )lumens, system efficacy ≥ 100 lm/W, LED lumen efficacy ≥ 120 lm/W, CCT 3000K~6500K, CRI >70, electronic driver, 10 kV in-built surge protection, Output open/short circuit protection, phase to phase protection, over-voltage protection, etc. as per IS-15885, THD<10%, PF ≥ 0.95, housed in pressure die cast aluminium housing including necessary fabrication for fixing of LED stree tlight in existing GI bracket i.e GI reducer all as per directed by Engineer-in-Charge. Havells Cat No. ENDURAPEARLNEOSL60WLED757SASYTOPC or equivalent as mentioned in the APPENDIX 'B' .

Qty : 905 No’s.