Dear sir,

Please find the Attachment and give your best rate of some item.

|  |  |  |  |
| --- | --- | --- | --- |
| **Sl.No** | **Description of Work / Item(s)** | **No.of Qty** | **Units** |
|  |  |  |  |
| 1.00 | Supply of 2 x 250W Crescent shaped LED flood light made of pressure die cast aluminium housing & having system lumen > 52000 Lumens, Heat resistant toughened glass, back opening driver compartment for ease of maintenance, Input voltage working range 140Vac to 300Vac, LEDs with induvial PMMA lens of "30 Degree beam angel" for better light disribution, Potted type driver for long life with short circuit, open circuit, High Voltage protection with Upper cut off limit of 100Vac & auto restart after stable voltage, Over temperature protection (driver to withstand till 60 Degree temp), Fitting have to withstand for 8 Hrs in case of 440 Vac fault, each driver have Internal surge protection 4KV Line -line & 6KV Line-earth & Potted type 5KV External surge protection, THD <10%, CCT: 5700+/-300K, PF> 0.95, Temp working range -10 Degree to 60 Degree C, IP66 Protection for dust & water, Driver efficiency > 90%, CRI>70, IK08 Protection, LM79 report from in house NABL Accredited lab, LM 80 Report, TDS (Crompton : LFLPI-500-CDL/30) (Dimension : 720mm x 420mm x 145mm) | 16.00 | No |
| 2.00 | Supply of 2 x 250W Crescent shaped LED flood light made of pressure die cast aluminium housing & having system lumen > 52000 Lumens, Heat resistant toughened glass, back opening driver compartment for ease of maintenance, Input voltage working range 140Vac to 300Vac, LEDs with induvial PMMA lens of "60 Degree beam angel" for better light disribution, Potted type driver for long life with short circuit, open circuit, High Voltage protection with Upper cut off limit of 300Vac & low voltage protection with lower cut off limit of 100Vac & auto restart after stable voltge, Over temperature protection (driver to withstand till 60 Degree temp), Fitting have to withstand for 8 Hrs in case of 440 Vac fault, each driver have Internal surge protection 4KV Line -line & 6KV Line-earth & Potted type 5KV External surge protection, THD <10%, CCT: 5700+/-300K, PF> 0.95, Temp working range -10 Degree to 60 Degree C, IP66 Protection for dust & water, Driver efficiency > 90%, CRI>70, IK08 Protection, LM79 report from in house NABL Accredited lab, LM 80 Report, TDS (Crompton : LFLPI-500-CDL/60) (Dimension : 720mm x 420mm x 145mm) | 8.00 | No |

Thanking you

**Name :- Manish Electricals**

**Add :- Kalpna Nagar C.P. Colony**

**7 No. Chouraha Morar**

**Gwalior - 474006**

**Ph. No. 0751-2463664**

**Fax No. 07514030948**